SECTION 028700

MERCURY REMEDIATION

USE THIS SECTION FOR PROJECTS WHERE MERCURY HAS BEEN IDENTIFIED AND REQIRES REMEDIATION AND DISPOSAL. INCLUDE MERCURY SURVEY REPORT IN THE APPENDIX. SEE INFORMATION AT THE END OF THIS SECTION.

PART 1   GENERAL

1.01	SUMMARY

A.	This Section specifies the procedures for the removal of mercury waste or mercury containing materials, protecting occupants and workers performing the remediation and prevention of migration of mercury contamination to adjacent areas.

B.	Examine all areas in which the remediation work is to be performed and make necessary investigation regarding completion of the work.

1.	Notify the Director’s Representative of any discrepancies found between the documents and the actual field conditions.

C.	Furnish all labor, materials, services, insurance, patents, and equipment necessary to perform the work of this contract.

1.	All work will be conducted in compliance with EPA, OSHA, and NYS regulations, any other applicable federal, state, and local regulations and in accordance with these specifications.

2.	In the event there is a conflicting point between these provisions, the most stringent one shall apply.

- The work of this contract involves the controlled removal and disposal of mercury waste or mercury contaminated construction materials, cleaning of contaminated surfaces and disposal of all waste from within the Work Zones in accordance with all applicable regulations, guidelines and as outlined in this specification.

E.	This is a level 2 mercury contamination, requiring prompt remediation.

1.	Concentration of mercury is between 1.0g/m3 and 10g/m3.

2.	Follow all the procedures listed in Part 3 of this Section.

USE PARAGRAPH ABOVE OR BELOW AS REQUIRED

F.	This is a level 1 mercury contamination, requiring immediate remediation.

1.	Concentration of mercury is equal to or greater than 10g/m3.

2.	Follow all the procedures listed in Part 3 of this Section.

1.02	RELATED WORK SPECIFIED ELSEWHERE

A.	Summary of the Work:  Section 011000.

B.	Construction Facilities and Temporary Controls:  Section 015000.

USE PARAGRAPH BELOW ONLY IF ASBESTOS IS PRESENT ON A SURFACE THAT WOULD BE DISTURBED DURING MERCURY REMEDIATION. INCLUDE REFERENCES TO ANY OTHER HAZARDOUS METERIAL THAT MY BE MIXED WITH MERCURY.

C.	Asbestos Abatement:  Section 028213.

D.	Mercury Survey Report:  In Appendix.

E.	Existing Hazardous Material Information:  Section 003126.

1.03	REFERENCES

A.	Occupational Safety and Health Administration (OSHA):

1.	Hazardous Waste Operations and Emergency Response, Title 29, Part 1910, Section 120 of the Code of Federal Regulations.

2.	Respiratory Protection, Title 29, Part 1910, Section 134 of the Code of Federal Regulations.

3.	Construction Industry, Title 29, Part 1926, of the Code of Federal Regulations.

4.	Hazard Communication, Title 29, Part 1910, Section 1200 of the Code of Federal Regulations.

5.	Specifications for Accident Prevention Signs and Tags, Title 29, Part 1910, Section 145 of the Code of Federal Regulations.

B.	U.S. Environmental Protection Agency (EPA):  www.epa.gov.

1.	U.S. EPA Region 5 – Mercury Response Guidebook.

C.	Center for Disease Control (CDC):  Air Pollution and Respiratory Health:  www.cdc.gov/page.do.

D.	American Board of Industrial Hygiene (ABIH):  www.abih.org.

1.04	DEFINITIONS

A.	Abatement/Remediation:  The process or procedure for removing and controlling hazardous material.

B.	Adequately Wetted:  Sufficiently wet, mixed, or coated with a detergent solution to prevent biological and dust dispersion during the movement of contaminated items and debris.

C.	Air Filtration Device (AFD):  A local exhaust HEPA equipped air filtration device capable of maintaining a negative pressure inside the work area and a constant air flow from adjacent areas into the work area exhausting clean filtered air outside the work zone.

D.	Air Testing:  The process of measuring inside mercury contamination and outside ambient conditions.

E.	Authorized Personnel:  Facility representative, and all other personnel who are authorized officials of any regulating agency, be it State, Local, Federal or Private entity who possess legal authority for enforcement or inspection of the remediation work.

F.	Barrier:  Any surface which seals off the work area to inhibit the movement of hazardous waste and contamination.

G.	Breathing Zone:  A zone forward of the shoulders and head with a radius of approximately 6 to 9 inches, which is the approximate area from which an individual would obtain their air for breathing purposes.

H.	CIH:  Certified Industrial Hygienist, certified by the American Board of Industrial Hygiene.

I.	Clearance Criteria:  Air testing clearance criteria shall be established that no single sample shall have levels greater than established by these specifications. Levels shall be recorded in g/m3.

J.	Construction Barrier:  Used for construction separation only.

1.	Does not prevent movement of mercury contamination.

2.	Constructed of 1/2 inch plywood and 2" x 4" studding spaced no greater than 24" o/c.

3.	Doorways:  (minimum), 3 ft. x 6 ft., and installed where required for ingress and egress.

4.	Install lock to secure the area when the Contractor is not on site.

K.	Contractor:  The Remediation Contractor who has demonstrated proficiency in the clean-up of regulated chemical or physical substances, proficient in environmental remediation and the clean-up of contaminated debris and/or infectious biological agents.

L.	Critical Barrier:  Two  layers of 6 mil polyethylene sheeting adhered in such a fashion that each layer is individually visible, and completely seals off the work area to prevent the distribution of hazardous waste into the surrounding areas that are not part of the work area.

M.	Decontamination Unit:  A serial arrangement of rooms or spaces for the purpose of separating the work area from the building environment.  This unit provides for entering the work site, returning to the clean environment, cleaning of persons, equipment, and movement of properly contained waste material.

N.	Disposal Bag:  A minimum 6 mil thick leak tight plastic bag used for packaging and transporting debris and hazardous waste from the work area to a disposal site.

O.	Facility:  Any institutional, commercial or industrial structure, installation or building.

P.	Facility Component:  Any building component, such as, but not limited to: structural steel, steel decking, ceiling grid, block and brick, floors, walls, ceilings, bar joists, light fixtures, ceiling hangers, studs, plates, insulation, and all other vertical and horizontal surfaces.

Q.	Fixed Object:  Mechanical equipment, electrical equipment, fire detection systems, alarms, and all other fixed equipment, furniture, fixtures or other items which cannot be removed from the work area.

R.	HEPA:  High Efficiency Particulate Absolute filtration efficiency of 99.97% down to 0.3 microns.  Filtration provided on specialized vacuums and air filtration devices to trap particles and infectious agents.

S.	HVAC:  Heating, Ventilation and Air Conditioning system.

T.	Moveable Object:  Equipment, furniture or other items in the work area which can be removed from the work area.

U.	Negative Pressure Ventilation System:  A system established for the work zone utilizing HEPA filtration capable of maintaining a negative pressure inside the work area and which creates a constant air flow from adjacent areas into the work area and exhausts clean filtered air outside the work zone.  Maintain a minimum of one complete air change every 15 minutes and 0.02 inches of water column pressure differential from the surrounding area.

V.	PPE:  Personal Protective Equipment.

W.	Remediation/Abatement:  The process or procedure for removing and controlling mercury contamination.

X.	Respirator:  Device designed to protect the wearer from the inhalation of harmful respirable dust, fumes, mists and infectious biological agents.

Y.	Separation Barrier:  Used for isolating contaminated work areas from non-contaminated occupied areas.

1.	Separation barriers shall be constructed of ½ inch plywood and 2 x 4 studding spaced no greater than 16" o.c. with two layers of 6 mil fire resistant polyethylene installed on both sides.

2.	A minimum 3 ft. x 6 ft. emergency escape kick-out panel shall be cut and secured into place with duct tape where required for emergency egress.

3.	This exit shall be clearly marked from the work area side and indicated on the emergency route document posted at the entrance to the work area.

Z.	Staging Area:  Site where Contractor maintains waste transfer airlock, where containerized waste has been placed, an outside site of material storage, equipment storage, construction trailer, etc.  These areas are off limits to unauthorized personnel and shall be clearly and visibly marked.

AA.	Structural Member:  Any load supporting member of a facility, such as, but not limited to: beams, decking, load supporting walls or any non-load supporting member, such as: ceilings, non-load supporting walls.

BB.	Visible Emissions:  Emissions containing particulate materials that are visually detectable without the aid of instruments.

CC.	Waste Transfer Airlock:  A system airlock constructed in such a manner as to prevent the free flow of air to areas outside of the work area and utilized for transferring containerized waste from inside to outside the work area.  The system shall be checked prior to use for negative air flow.

DD.	Water Column (w.c.):  Means a unit of measurement for pressure differential expressed in inches of water column.  Maintain 0.02 inches of w.c. in occupied facilities.

EE.	Wet Cleaning:  The process of eliminating biological contamination from building surfaces and objects by using cloths, mops, or other cleaning devices which have been dampened with  detergent solution.

FF.	Work Area:  The area where the related work or decontamination operations are performed which is defined and or isolated to prevent the spread of mercury.

GG.	Abbreviations for organizations and regulating authorities that may appear in this document:

1.	ACGIH:  American Conference of Governmental Industrial Hygienists

1330 Kemper Meadow Drive

Cincinnati, Ohio  45240-1634

2.	AIHA: American Industrial Hygiene Association

2700 Prosperity Avenue

Suite 250

Fairfax, Virginia  22031

3.	ANSI:	American National Standards Institute

1430 Broadway

New York, New York 10018

212-354-3300

4.	ASTM:  American Society for Testing and Materials

1916 Race Street

Philadelphia, PA  19103

215-299-5400

5.	CFR:  Code of Federal Regulations

Government Printing Office

Washington, DC  20402

6.	USEPA:  United States Environmental Protection Agency

401 M Street SW

Washington, DC  20460

202-382-3949

7.	NIOSH:  National Institute for Occupational Safety and Health

Building J.N.E. Room 3007

Atlanta, Georgia  30333

8.	OSHA: 	Occupational Safety and Health Administration

200 Constitution Avenue

Washington, DC  20210

1.05	SUBMITTALS

A.	Quality Control Submittals:

1.	Work Plan:  Submit one copy of the work plan required under Quality Assurance Article.

2.	Waste Transporter Permit:  One copy of transporter's current waste transporter permit.

USE SUBPARAGRAPH BELOW IF THE CONTRACTOR CAN TAKE HIS OWN SAMPLES.  DELETE PARAGRAPH IF THE CONTRACTOR CAN NOT TO DO HIS OWN TESTING OR IF TESTING IS NOT NECESSARY

3.	Testing Laboratory Data:  Name and address of the proposed testing laboratory.

4.	Mercury Remediation Contractor’s Qualifications Data:

a.	Name of remediation contractor, business address, and telephone number.

b.	Number of years in business.

c.	Number of years performing mercury remediation.

d.	Names, address, and contact phone numbers of five projects of similar size and complexity in which contractor has performed mercury remediation work in the last 5 years.

5.	Mercury Remediation Worker Qualifications Data:

a.	Name of each person who will be performing the work and their employer’s name, business address and telephone number.

B.	Mercury Remediation Work Closeout Submittals:

1.	For projects requiring sampling and monitoring provide an assessment report compiled by an experienced Industrial Hygienist.

2.	Disposal Site Receipts:  Copy of each receipt showing the mercury containing materials have been properly disposed.

1.06	QUALITY ASSURANCE

A.	Regulatory Requirements:  Comply with the referenced standards.

B.	Pre-Work Conference:  Before the Work of this Section is scheduled to commence, a conference will be held by the Director's Representative at the Site with the Contractor and the hazardous material remediation Subcontractor (if any) for the purpose of reviewing the Contract Documents, discussing requirements for the Work, and reviewing the Work procedures.

C.	Mercury Containing Material Removal Work Plan:  Before the physical Work begins, prepare a detailed Mercury Containing Material Removal Work Plan.

1.	The work plan shall include, but not be limited to, the location, size, and details of mercury control areas, sequencing of mercury containing material handling, work procedures, types of equipment, crew size, estimated completion time and emergency procedures for fire and medical emergencies.

D.	Mercury Remediation Contractor Qualifications:

1.	Pre-qualified in environmental abatement discipline or waste removal toxic/ hazardous classification by the State of New York Department of Environmental Protection.

2.	The firm performing the work of this section shall have been regularly engaged in mercury remediation work for a minimum of 3 years, and shall have completed 5 similar projects of size and complexity.

E	Mercury Remediation Worker Qualifications:  The person performing mercury remediation and their supervisor shall be personally experienced in the type of work, completed a 40 hour Hazardous Waste Operations & Emergency Response course (HAZWOPER) in accordance with OSHA 1910.120 and with a minimum of one year experience.

USE PARAGRAPH BELOW IF SAMPLING IS REQUIRED

F.	Testing Lab Qualifications:  The proposed testing lab shall be New York State Department of Health Environmental Laboratory Approval Program (NYS ELAP) certified.

1.07	PROJECT CONDITIONS

A.	Shut-down of Air Handling System:  Complete the Work of this Section within the time limitation allowed for shutdown of the air handling system serving the work area.

1.	The air handling system will not be restarted until approval of the post-work dust-wipe testing following the last cleaning.

B.	Cover and seal all fin-tube radiator covers, diffusers, duplex outlets, speakers, smoke and heat detectors etc with two layers of polyethylene sheeting.

1.	Prevent hazardous material from entering hard to clean areas within any ductwork inside the containment area.

2.	Items judged to be too difficult to protect may be disconnected, removed and replaced at contractor’s option.

C.	Remove or encase all movable equipment in the work area with two layers of six mil fire retardant polyethylene sheeting.

D.	Bag all loose items and sample for contamination.

1.08	DELIVERY AND STORAGE

A.	Deliver HgX or Mercsorb in manufacturer’s original sealed and labeled containers, if used.

B.	Store the above referenced materials in compliance with manufacturer’s printed instructions.

1.09	PERSONAL PROTECTIVE CLOTHING AND EQUIPMENT

A.	Workers must wear protective suits, protective gloves, eye protection and a NIOSH certified full face respirator with mercury vapor filter, Self Contained Breathing Apparatus (SCBA), or supplied air based on level of contamination and recommendations of the work plan and industrial hygienist.

1.	Respiratory protection shall be in accordance with OSHA regulation 1910.134 and ANSI Z88.2.

B.	Workers must be trained, have medical clearance and must have recently received pulmonary function test (PFT) and respirator fit tested by a trained professional.

1.	The use of respirators must also follow a complete respiratory protection program as specified by OSHA.

C.	Workers must wear long gloves made out of rubber, neoprene, nitrile or PVC.

1.	Safety glasses or goggles with open vent holes are not acceptable.

2.	Dust masks will not be allowed regardless of certification or TC approval number.

1.10	HEALTH AND SAFETY

A.	Accident Prevention:  In order to protect the lives and health of his employees, comply with all pertinent provisions of the latest edition of the "Manual of Accident Prevention in Construction" issued by the Associated General Contractors of America, Inc.

1.	Maintain an accurate record of all accidents which occur during the project.

2.	An injury or loss of life must be immediately reported by the Contractor to the Director’s Representative.

3.	Provide a copy of the Contractor's report to his insurer of an accident must be provided to the Director’s Representative.

B.	Emergency Response:  Establish an Emergency Response Team made up of members of his work force.

1.	Team members shall be trained, organized, and capable of responding in the event of an accident, fire, or other emergency.

2.	Designate a site Safety Coordinator to train team members regarding the location and use of site-specific fire/life safety equipment.

3.	As a minimum requirement, members of the Emergency Response Team shall be knowledgeable in standard first aid and CPR techniques, fire extinguisher use, and evacuation procedures.

C.	Workmen Protection:  Provide and maintain all safety measures necessary to properly protect workmen.

D.	Emergency Actions:  In an emergency affecting the safety of life, the work, or adjoining property, the Contractor, to prevent such threatened loss or injury without special instruction or authorization from the Director’s Representative, is hereby permitted to act at his discretion.

E.	Hazard Communication Act:  Comply with the Hazard Communication Standard promulgated by the Occupational Safety and Health Administration (OSHA No. 29 CFR 1910.1200).

1.	This program ensures that all employers provide the information they need to inform and train employees properly and to design and put in place employee protection program.

2.	It also provides necessary hazard information to employees so they can participate in, and support, the protective measures needed at their work place.

3.	Ensure that labels or other forms of warning are legible in English.

4.	Employer having employees who speak other languages may add the information in their languages.

5.	See OSHA 29 CFR 1910.1200 for more details.

F.	Due to the potential elevated levels of contamination, apprize their supervisor and crew with regard to the potential health risks associated with mercury exposure and of the proper work procedures that must be followed.

G.	Submit documentation on each individual that has the potential of entering the work area on their behalf, to verify that they have received recent pulmonary function testing (PFT) and respiratory fit testing.

H.	Where in the performance of the work, workers, supervisory personnel, or sub-contractors may encounter, disturb, or otherwise function in the immediate vicinity of contaminated items and materials, all personnel shall take appropriate continuous measures as necessary to protect all ancillary building occupants from the potential hazard of exposure to hazardous material.

1.	Such measures shall include the procedures and methods described herein and shall be in compliance with all applicable regulations of Federal, State and Local agencies.

1.11	FIRE PROTECTION AND EMERGENCY EGRESS

A.	Provide security and safeguarding of all areas turned over by the Facility to the Contractor.  Notify his workers and other building occupants of the means of egress in case of emergency.

B.	Establish emergency and fire exits from the work area.  First aid kit, 2 full sets of protective clothing and respirators shall be provided for use by qualified emergency personnel in the clean room of the decontamination facility.

C.	Provide fire watch and logbook throughout the entire term of the project, to protect against fire and unauthorized entry into and around the work area.

1.	Any intrusion or incident shall be documented in the log book.

2.	Fire watch personnel shall be present during off-hours when the containment is still active and Negative Pressure Ventilation System (HEPA Air Filtration Device) is active.

PART 2  PRODUCTS

2.01	AIR FILTRATION UNIT

A.	Type:  Comply with ANSI Z9.2 (1979), Local Exhaust Ventilation.  The final filter in each unit shall be of the HEPA type.

1.	Certified by the manufacturer to have an efficiency of not less than 99.97 percent when challenged with 0.3 micron particles.

2.	Provide proof that filters are new and unused from previous projects.

B.	Equip the system with the following:

1.	An automatic shutdown that will stop the fan in the event of a rupture in the HEPA filter or blocked air discharge.

2.	Warning lights and/or alarms to indicate an excessive pressure drop across the filters or an insufficient pressure drop across the filters.

3.	A non-resettable elapsed time meter to indicate the total accumulated hours of operation.

4.	A gauge or manometer to measure the pressure drop across the filter.

2.02	DISPOSAL BAGS

A.	Type:  Minimum 6 mil in thickness, clear in color and preprinted with a Caution Label.

USE ARTICLE BELOW AS REQUIRED

2.03	ENCAPSULATING MATERIAL

A.	Type:  Approved by UL for use in class 1A buildings and shall have composite fire and smoke hazard ratings as tested under procedure ASTM E- 84, NFPA 255 and UL 723:

1.	Flame Spread:  25.

2.	Smoke Developed:  50.

2.04	EQUIPMENT

A.	Temporary lighting, heating, hot water heating units, ground fault interrupters, and all other equipment on site shall be UL listed and shall be safe, proper, and sufficient for the purpose intended.

B.	All electrical equipment shall be in compliance with the National Electric Code.  Attention is specifically called to Article 305 Temporary Wiring.

C.	Mercury Vapor Analyzer:  Acceptable models; Jerome MVA, Lumex RA+ Mercury Vapor Analyzer, VM-3000 Mercury Vapor Monitor and Nippon Portable Mercury Survey Meter.

2.05	FIRST AID KITS

A.	Maintain adequately stocked first aid kits in the Clean Room and Work Zone, in accordance with OSHA requirements.

2.06	HIGH EFFICIENCY PARTICULATE AIR (HEPA) FILTERS

A.	Type:  Individually tested and certified by the manufacturer to have an efficiency of not less than 99.97 percent when challenged with 0.3 micron particles, in accordance with Military Standard Number 282 and Army Instructional Manual 136-300-175A.  Each filter shall bear a US 586 label to indicate ability to perform under the specified conditions.

B.	Mark each HEPA filter with the name of the manufacturer, serial number, air flow rating, efficiency and resistance, and the direction of air flow.

2.07	PLASTIC SHEETS

A.	Type:  Fire retardant plastic sheets of polyethylene, which have a minimum thickness of 6 mil true grade, unless otherwise specified.

1.	Initial Floor Protective Layer:  Reinforced plastic sheets of polyethylene, which has a minimum thickness of 10 mil true grade.

2.08	PLYWOOD

A.	Type:  Fire-rated CDX plywood, which is at minimum one half inch in thickness.

2.09	RESPIRATORS

A.	Type:  Approved by the Mine Safety and Health Administration (MSHA), Department of Labor, or the National Institute for Occupational Safety and Health (NIOSH), Department of Health and Human Services.

1.	If filtered respirators are used, provide the appropriate filter for mercury vapor.

2.10	SEALANTS

A.	Combination Fire Stop Foam and Fire Stop Sealant:

1.	Dow Corning Fire Stop Foam and Dow Corning Fire Stop Sealant.

2.	Apply in accordance with manufacturer's recommendations.

2.11	STUDS

A.	Type:  2" x 4" fire-treated wood studs or metal studs.

USE ARTICLE BELOW FOR ALL PROJECTS OTHER THAN SMALL PROJECTS.

2.12	SUPPLIED AIR SYSTEM

A.	At all times, air supplied to the type "C" respirators shall be Grade "D" Breathable Air as described by OSHA Regulation 29 CFR 1910.134(d)(1), containing less than the following:

1.	Carbon Monoxide:  20 parts per million.

2.	Carbon Dioxide:  1,000 parts per million.

3.	Condensed Hydrocarbons:  5 milligrams per cubic centimeter.

4.	Objectionable odors:  None.

B.	Provide a minimum of one hour of reserve air for emergency evacuation.

1.	Post in the Work Zone, emergency evacuation procedures to be followed in the event of breathing air system failure.

2.	Explain procedures to all workers prior to commencement of the Work.

C.	Water content shall be less than 66 parts per million in order to protect the air purification unit.

1.	Certify the air quality of the system prior to beginning of  remediation work and every two weeks during hazardous material abatement Work by an independent laboratory certified by the American Industrial Hygiene Association - Environmental Microbiology Laboratory Accreditation Program (AIHA-EMLAP) accredited laboratory for analysis.

2.	Collect samples under the supervision of a Certified Industrial Hygienist.  Submit copies of certified test results to the Director’s Representative within 5 days of the sample collection.

2.13	VACUUM CLEANERS

A.	Type:  Mercury vacuums equipped with HEPA filters.

PART 3   EXECUTION

EDIT ARTICLE BELOW AS REQUIRED.  COORDINATE WITH HAZMAT DESIGNER.

3.01	PRE-REMEDIATION TESTING

USE PARAGRAPH BELOW FOR SMALL PROJECTS.

A.	Bulk Sampling:  Individual trained in collecting bulk or surface samples shall be utilized.

1.	A lab certified to analyze the samples shall perform the testing and analysis.

2.	Employ the services of an industrial hygienist before the start of the project, who specializes in hazardous material remediation for Analysis and Report.

USE PARAGRAPH BELOW FOR LARGE PROJECTS, LITIGATION IS INVOLVED, OR IF OCCUPANTS ARE EXPERIENCING SYMPTOMS WHICH MAY BE RELATED TO MERCURY EXPOSURE. AIR MONITORING IS ALSO REQUESTED FOR COMPARITIVE PURPOSES WITH OUTSIDE AIR.

B.	Air Sampling:  Air sampling shall determine the extent and scope of contamination.

1.	Individual trained in collecting air samples shall be utilized. A lab certified to analyze the samples shall perform the testing and analysis.

2.	The contractor shall employ the services of an industrial hygienist before the start of the project, who specializes in hazardous material remediation for Analysis and Report.

3.02	EMPLOYEE PROTECTION

A.	Comply with all applicable Occupational Safety and Health Administration (OSHA) Requirements. Also see section 1.9.

USE ARTICLE BELOW FOR PROJECTS WHERE THE CAUSE AND QUANTITY OF SPILL IS NOT KNOWN AND HAS NOT BEEN CORRECTED. USE FOR EMERGENCY PROJECTS WHERE NECESSARY.

3.03	ASSESMENT AND REPAIR OF DEFECTS

A.	The cause of the mercury contamination shall be identified and fixed before any work commences.  Determine the amount of mercury that was spilled.

3.04	PREPARATION OF WORK AREA

A.	Shut down all HVAC systems running through the work area shall be shut down or isolated if possible to prevent the spread and migration of contamination to the adjacent non contaminated areas or surfaces.

B.	Seal all ventilation openings or any other openings in the work area with six mil fire retardant polyethylene.

C.	The work area shall remain unoccupied until the completion of the remediation project.  All areas immediately adjacent to the work area shall be vacated for large contaminated area abatement.

D.	Isolate the work area shall be isolated from non work areas with two layers of six mil fire retardant polyethylene.

1.	All surfaces that are contaminated shall be within the containment area.

2.	Wrap non removable items in two layers of six mil polyethylene.

3.	Establish an airlock chamber at the exit of the work area.

4.	Passageways shall consist of covering flap cover at the entrance opening.

E.	Maintain Work area under negative pressure with HEPA filtered units exhausting outside the building.

1.	Units shall maintain at least four air changes an hour and shall not exhaust near any building intake openings.

USE ARTICLE BELOW FOR LARGE PROJECTS

3.05	DECONTAMINATION FACILITY AND SEQUENCE

A.	In an approved designated location, attached to the work site, place a decontamination unit as specified where the workers may be able to decontaminate and change into clean clothing upon exiting the work area.

1.	Location of the clean area/decontamination unit shall require the approval of the Director’s Representative.

2.	Contractor shall obtain approval of the Director’s Representative for location of staging and storage area(s).

B.	Installation of Decontamination Units:

1.	Construct three stage decontamination unit which directly adjoins the work area.

2.	The three stage unit shall include an equipment room, shower room (with hot and cold running water) and clean room.

3.	The three stage decontamination units shall be operational throughout all phases of work.

4.	Have on hand at all times sufficient soap, disposable towels, etc.

5.	Provide clean change area in accordance with OSHA Regulations.

C.	Typical decontamination sequence for workers at the end of their shift shall be as follows:

1.	Before leaving the immediate work area, the person shall remove all gross contamination and debris.

2.	The worker shall then proceed to the equipment room and remove the disposable clothing including protective suit, hood, gloves and booties.  The respirator shall remain on.

3.	The worker shall then proceed to the shower room.  Respirators shall be taken off last to prevent inhalation of contaminated dust and debris.

4.	After showering, the worker shall proceed to the clean room and dress in clean street clothing prior to exiting.

5.	Respirators shall be picked up, washed thoroughly, and disinfected as required, inspected, wrapped and stored in the clean room for the next day's work.

6.	There shall be no smoking, eating, or drinking in a contaminated area (shower room, equipment room and designated work area).  Follow all facility regulations regarding smoking areas.

7.	Everyone entering the work zone shall follow the decontamination procedure completely every time they enter or leave the designated work area.

8.	All water used by the Contractor during remediation activities shall be collected and passed through an appropriate water filtration system prior to being discharged into the sanitary sewer.

a.	Coordinate with Director’s Representative to determine the acceptable location(s) to access the sanitary sewer.

b.	Provide connection to the sanitary sewer, and for providing piping, pumps, water filtration systems, and other items necessary to collect, transport, filter, and dispose of the wastewater.

3.06	CLEANING AND DECONTAMINATION OF CONTAMINATED SURFACES

COORDINATE LOCATIONS WITH THE DESIGNER AND IDENTIFY ON THE DRAWINGS

A.	The areas that require mercury remediation, locations and approximate quantities are shown on drawings.

1.	Be conscious of adjacent visibly contaminated areas.

2.	If any, report condition to the Director’s Representative and include in the remediation work plan upon approval.

B.	Follow the guidelines specified for all mercury remediation projects.

EDIT TABLE BELOW FOR THE LEVEL OF CONTAMINATION

| Guidelines For Remediating Building Materials ContaminatED WITH MERCURY |  |  |  |
| --- | --- | --- | --- |
| Material | Method | PPE | Containment |
| LEVEL 1 or 2 MERCURY REMEDIATION – See definition in subsection 1.01.E |  |  |  |
| Books and papers | 3, 4 |  |  |
| Carpet and backing | 1, 3, 4 |  |  |
| Concrete or cinder block | 1, 2 |  |  |
| Hard Surface, Porous flooring (Linoleum, ceramic, vinyl tile) | 1, 2 | In accordance with OSHA 29 CFR 1910.120 App. B | In accordance with OSHA 29 CFR 1910.120 (g) |
| Non-porous hard surfaces (Plastic, metals) | 1, 2 |  |  |
| Drapers | 1, 3, 4 |  |  |
| Drywall and gypsum board | 1, 4 |  |  |
| Wood surfaces | 1, 2 |  |  |

C.	Method 1:  Mercury Vacuum with HEPA filter.

1.	Use vacuum cleaners designed and approved to collect mercury.

2.	Use mercury vacuum cleaners to remove mercury from floors and hard surfaces.

3.	Do not use this method to vacuum porous materials and/or when they are dry.

4.	Seal the filter in polyethylene bags and properly disposed.

D.	Method 2:  Damp Wipe.

1.	Wipe surfaces with clean water and HgX solution.

2.	For wood use wood floor cleaner and scrub as required.

3.	Do not damp wipe Porous surfaces.

4.	Dry all surfaces quickly and thoroughly.

E.	Method 3:  Bag Material and Sample with a mercury vapor analyzer.

1.	Objects that do not contain mercury may be returned after remediation.

2.	Otherwise use Method 4 below.

F.	Method 4:  Discard mercury containing materials.

1.	Double bag materials that are not salvageable with six mil polyethylene sheeting and dispose.

3.07	DECONTAMINATION OF WORK AREA

A.	Once wet wiping is complete and required drying time is allowed, HEPA vacuum all surfaces.

B.	Use fans following the completion of HEPA vacuuming of all surfaces.

1.	Fans shall be used to thoroughly dry the surfaces that were cleaned.

2.	Do not use dehumidifiers for drying the surfaces.

3.08	CLEANING CRITERIA

A.	The areas are considered clean when air and wipe samples show levels below action level.

1.	For spills reported to the DEC, a closure report is to be issued so the spill number can be closed out.

3.09	CERTIFICATION OF CLEANING

A.	Prior to removal of the isolation barriers if any were erected, Director's Representative will employ the services of an independent testing lab that has an Industrial Hygienist (Mycologist) on board.

1.	The Director will obtain an affidavit and report stating that the final tests confirm to all applicable standards prior to the isolation barrier removals.

2.	Schedule a walk-through inspection with the Director’s Representative and obtain their written approval.

USE PARAGRAPH BELOW FOR LEVEL 1 & 2 PROJECTS, OR IF LITIGATION IS INVOLVED.

B.	Bulk Sampling:

1.	Individual trained in collecting bulk or surface samples shall be utilized.

2.	A lab certified to analyze the samples shall perform the testing and analysis.

3.	The Director will employ the services of an industrial hygienist before the start of the project, who specializes in hazardous material remediation for Analysis and Report.

USE PARAGRAPH BELOW FOR LEVEL 1 & 2 PROJECTS, OR IF LITIGATION IS INVOLVED. AIR MONITORING IS ALSO REQUESTED FOR COMPARITIVE PURPOSES WITH OUTSIDE AIR LEVELS.

C.	Air Sampling:  Air sampling shall determine the extent and scope of contamination.

1.	Director's Representative will employ the services of an independent testing lab that has an Industrial Hygienist (Mycologist) on board.

2.	Individual trained in collecting bulk or surface samples shall be utilized.

3.	A lab certified to analyze the samples shall perform the testing and analysis.

4.	The Director will employ the services of an industrial hygienist before the start of the project, who specializes in hazardous material remediation for Analysis and Report.

D.	Air monitoring shall be performed by the Industrial Hygienist with the HVAC system in operation.

1.	Air testing shall not be performed if contaminated debris or dust is present or if internal surfaces appear wet.

2.	Repeat the final cleaning procedure if visual inspection fails, if so instructed by the Industrial Hygienist.

E.	Make provisions to allow for up to a minimum of 8 hours turn-around time between the taking of the clearance air samples and the receipt of air sample results.

1.	During this period, the work area enclosures and engineering controls specified shall continue in operation and shall meet the Contract specified parameters.

2.	If the Industrial Hygienist determines the testing results to be unsafe for re-occupancy then return to the work areas to conduct a full recleaning.

F.	One air sample shall be taken inside the containment area for each 2,500 square feet of work area.

1.	At a minimum, this shall include one outside ambient air sample for comparison and a quality control blank to be collected by the air sampling technician.

2.	Submit all samples shall be submitted to an American Industrial Hygiene Association - Environmental Microbiology Laboratory Accreditation Program (AIHA-EMLAP) accredited laboratory for analysis.

G.	The air sampling technician shall collect final air samples.

H.	For expediency, the Independent Testing Lab shall inform the Contractor verbally of air sample results.

1.	If air sample results of the Air-O-Cell cassettes meet the clearance criteria established by the Director or Industrial Hygienist, the Contractor shall be informed that they may proceed to the next step.

2.	If air sample results do not meet the clearance criteria established, reclean the work area as specified.

3.	The Industrial Hygienist shall perform a thorough inspection of the work area and all containment procedures in order to ensure the efficacy of additional cleaning procedures.

4.	Upon completion of the recleaning, the Industrial Hygienist shall perform resampling.

5.	Do not proceed in taking down enclosures or removing engineering controls until the specified air clearance criteria have been met.

I.	All clean area and final work area visual inspections will be performed by the Director’s Representative.

1.	The purpose of this visual inspection is to verify completeness of remediation and cleaning procedures as specified.

3.10	POST REMEDIATION CLEANING

A.	At the conclusion of Hazardous Material decontamination work, after visual inspection, approval and passing of air clearance testing as specified, clean all ladders, scaffolds, and other equipment used during work.  Clean as specified.

B.	The protective plastic enclosures shall also be cleaned as per Specifications.

1.	This plastic, along with all wipe cloths, shall be disposed of as contaminated waste and placed into 6 mil plastic waste bags for disposal.

C.	Similarly, all plastic used to seal doors, windows, vents, or non-removable items shall be cleaned as per Specifications, removed and placed into 6 mil plastic waste bags for disposal.

D.	Upon notification from the Industrial Hygienist that the air testing results meet clearance criteria, the contained area and decontamination room shall be HEPA vacuumed and cleaned with a detergent solution prior to the removal of the isolation barrier.

1.	Leave all areas dry and visibly free from contamination and debris.

3.11	REMOVAL OF CONTAINMENT

A.	Removal of containment and engineering controls for reoccupancy shall not be permitted in any area where laboratory analysis indicates levels greater than the exterior control samples.

1.	Levels above the specified clearance criteria shall require recleaning and further decontamination as per Specifications.

B.	There shall be no surfaces that show visible dust or growth of microorganisms.

3.12	DISPOSAL OF MERCURY-CONTAINING/COATED MATERIAL AND RELATED DEBRIS

A.	Double bag building materials and furnishings that are contaminated with mercury and are not salvageable using 6 mil polyethylene sheeting.

B.	Seal all bags air tight to prevent dispersion of mercury contamination throughout the building.

C.	Transport and dispose of mercury containing material in accordance with the standards referenced in Part 1 of this Section.  Materials can usually be discarded as ordinary construction waste.

D.	The waste hauler must possess a valid solid waste transporter registration issued by the New York State Department of Environmental Conservation.

1.	A licensed solid waste transporter shall be a commercial collector/hauler, or the Contractor if so registered.

E.	Prior to final payment, supply appropriate chain of custody and disposal tickets or other documentation that indicates the landfill to which the waste was transported.

3.13	RESTORATION

A.	At the completion of the project remove temporary decontamination facilities and restore area designated for these facilities to its original condition or better.

END OF SECTION

THE REMAINDER OF THIS DOCUMENT IS FOR INFORMATION ONLY; NOT TO BE INCLUDED IN THE PROJECT SPECIFICATION.

INFORMATION FOR THIS SECTION WAS DERIVED FROM U.S. EPA MERCURY RESPONSE GUIDEBOOK – SECTION 5. THE GUIDEBOOK PRIMARILY DEALS WITH CONTAMINATION IN RESIDENTIAL SETTINGS BUT THE ACTION LEVELS AND REMEDIATION METHODS ARE THE SAME. THE SPECIFICATION IS SET UP WITH THE ASSUMPTION THAT THE CONTAMINATION IS PRE-EXISITING AND THEREFORE THE REFERRAL AND RECONNASSANCE PHASES OUTLINED IN THE RESPONSE GUIDBOOK WILL BE CONDUCTED BY TERM CONTRACT TESTING AGENCIES DURING THE DESIGN PHASE OF THE PROJECT. COORDINATE THE HAZARDOUS MATERIAL SAMPLING WITH YOUR TEAM HAZ MAT DESIGNER.

THERE ARE 3 LEVELS OF MERCURY CONTAMINATION:

- LEVEL 1 - REQUIRING IMMEDIATE REMEDIATION. CONCENTRATION OF MERCURY IS EQUAL TO OR GREATER THAN 10G/M3.

- LEVEL 2 - REQUIRING PROMPT REMEDIATION. CONCENTRATION OF MERCURY IS BETWEEN 1.0G/M3 AND 10G/M3.

- LEVEL 3 – NO ACTION REQUIRED. CONCENTRATION OF MERCURY IS EQUAL TO OR LESS THAN 1.0G/M3.

BELOW ARE SAMPLES OF LEAD CONCENTRATIONS AS REPORTED BY IDEM – INDIANA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT IN THEIR MERCURY SPILL INFORMATION AND CLEANUP GUIDANCE, DATED SEPTEMBER 2002:

- A FLUORESCENT LIGHT BULB CAN CONTAIN BETWEEN .01 AND .04 GRAMS OF MERCURY.

- A THERMOMETER  CAN CONTAIN BETWEEN .5 AND .7 GRAMS OF MERCURY.

- A THERMOSTAT CONTAINS APPROXIMATELY 3 GRAMS OF MERCURY.

- A SPHYGMOMANOMETER (BLOOD PRESSURE MEASURING DEVICE) CONTAINS HUNDREDS OF GRAMS OF MERCURY.

IN ADDITION TO THE PRODUCTS ABOVE, MERCURY HAS BEEN FOUND DURING THE REMOVAL OF SYNTHETHIC RUBBER GYM FLOORS.

IN NEW YORK STATE, THE DEC REQUIRES REPORTING OF SPILLS GREATER THAN ONE POUND (EQUAL TO TWO TABLESPOONS). SOME COUNTIES REQUIRE THE REPORTING OF ALL SPILLS, NO MATTER THE AMOUNT. ONCE NOTIFIED, DEC WILL ASSIGN A SPILL NUMBER. AT THE COMPLETION OF REMEDIATION, A CLOSURE REPORT WILL NEED TO BE ISSUED BEFORE DEC WILL CLOSE OUT THE SPILL NUMBER. THE CLOSURE REPORT IS TO CONSIST OF A DESCRIPTION OF METHODS OF REMEDIATION, PRE AND POST SAMPLING AND DISPOSAL MANIFESTS. CONSULT WITH THE INDUSTRIAL HYGIENIST FOR THE FORMAT OF THE CLOSURE REPORT.

1OZ. EQUALS 28.35 GRAMS

1LB. EQUALS 454 GRAMS

END OF INFORMATION