D&C  JEB/ME:dja
ALLOWABLE STRESS DESIGN


SECTION 051200
STRUCTURAL STEEL

PART 1   GENERAL

EDIT SECTION NUMBERS IN ARTICLE BELOW AS REQUIRED.
1.01
PRODUCTS FURNISHED BUT NOT INSTALLED UNDER THIS SECTION


A.
Anchor Bolts:  Installed under Section 033000 or 033001.


B.
Loose Bearing Plates:  Installed under Section 042000 or 042113 and 042200.


C.
Loose Lintels:  Installed under Section 042000 or 042113 and 042200.

EDIT SECTION NUMBERS IN ARTICLE BELOW AS REQUIRED.
1.02
RELATED WORK SPECIFIED ELSEWHERE


A.
Steel Joists:  Section 052116 or 052119.


B.
Steel Decks:  Section 053100 or 053101.


C.
Field Painting:  Section 099101.


D.
Concrete Fill for Columns:  Section 033000 or 033001.

1.03
REFERENCES


A.
Except as shown or specified otherwise, the Work of this Section shall meet the requirements of the following:



1.
Design, Fabrication, and Erection:  “Specification for Structural Steel Buildings, Allowable Stress Design and Plastic Design”, June 1, 1989, by the American Institute of Steel Construction (AISC Specification).



2.
Standard Practice:  Fabrication and erection practices shall comply with the “Code of Standard Practice for Steel Buildings and Bridges”, June 10, 1992, by the American Institute of Steel Construction (AISC Code).



3.
Welding:  Welding shall comply with the provisions of the “Structural Welding Code - Steel, AWS D1.1”, by the American Welding Society (AWS Code).



4.
High-Strength Bolting:  High-strength bolting shall comply with the “Specification for Structural Joints Using ASTM A 325 or A 490 Bolts” approved by the Research Council on Structural Connections of the Engineering Foundation on November 13, 1985 (Specification for Structural Joints).



5.
Cleaning Steel:  Comply with the appropriate specifications (SSPC SP-X) by the Steel Structures Painting Council.

1.04
DEFINITIONS


A.
AISC Manual:  Where reference is made to the AISC Manual, it shall mean the Manual of Steel Construction, Ninth Edition, of the American Institute of Steel Construction.

1.05
REQUIREMENTS FOR CONNECTIONS


A.
General:



1.
Except where Type 1 (rigid-frame) or Type 3 (semi-rigid framing) connections are indicated, the design has been prepared on the basis of Type 2 (simple or unrestrained) connections, complying with the provisions of Section A2.2 of the AISC Specification.



2.
Do not use connection details which depend upon sharing the stress between any combination of high-strength bolts in bearing-type connections and welds.



3.
Size connections for the loads indicated on the Drawings. If the loads are not indicated, use a connection whose capacity is half the total uniform load capacity shown in the “Allowable uniform loads in kips for beams laterally supported” tables in the AISC Manual for the given shape, span, and steel specification of the beam in question, unless otherwise indicated.



4.
Delete Paragraph J 1.9. of the AISC Specification.  Whenever axially loaded members are connected by groups of welds or bolts not located symmetrically with respect to the gravity axis or axes of the connected member, the welds or bolts shall resist both the axial load and the moment produced by their eccentricity in the plane of the connection.




a.
For end connections of axially loaded angles not subject to repeated variation in stress, fillet welds may resist axial load only, with the following limitations:  The length of fillet weld at the heel of the angle shall be not less than 1/2 nor more than 2/3 of the total length required for the axial load.  The length of fillet weld at the toe of the angle shall be not less than 1/3 nor more than 1/2 of the total length required for the axial load.



5.
All bolted connections shall have a minimum of two bolts.


B.
Shop Connections:  Unless otherwise indicated, all shop connections shall be welded or high strength bolted. Field connections required to be welded or fully-tensioned high-strength bolted shall meet the same requirements when fabricated in the shop.


C.
Field Connections:



1.
The following field connections shall be welded or fully-tensioned high-strength bolted as shown or noted on the Drawings or, when not shown or noted, shall be either welded or fully-tensioned high-strength bolted at the Contractor’s option:




a.
Column splices.




b.
Roof truss splices.




c.
Column bracing.




d.
Connections for supports of machinery.




e.
All connections of  trusses to columns .




f.
All connections of eave struts, eave purlins, first interior purlins, ridge beams, and ridge purlins to rigid frames and trusses.



2.
All other bolted field connections need only be tightened to the snug tight condition.



3.
When steel members of any cross section are to be spliced by welding in the field, a detailed welding procedure shall be submitted to the Director for approval.  The procedure shall be detailed on shop drawings, submitted and approved prior to the fabrication of structural steel.  The detailed field welding procedure shall include the method of supporting members during welding.  All field welded splices shall be subject to non-destructive testing, Radiographic Testing (RT), or Ultrasonic Testing (UT), as determined by the Director.  Field splice locations, when specifically shown on contract documents, shall not be relocated nor shall splices be added without written approval of the Director.


D.
Standard Beam Connections:



1.
Unless otherwise shown on the Drawings or required in the Specifications, all beam connections shall be framed in accordance with Part 4 of the AISC Manual, with sizes and lengths of angles and welds and with fastener spacings as shown therein.



2.
Standard beam connections shown on the Drawings shall be fabricated as detailed. Substitutions will not be approved.


E.
Special Beam Connections:



1.
Where special conditions make it impracticable to provide connections complying with Paragraphs A thru D, and no details for such connections are shown on the Drawings, special connections shall be used.  Such special connections shall, in general, comply with the provisions of the AISC Manual.



2.
Typical details of proposed special connections shall be shown on the job standards.



3.
Special connections shown on the Drawings shall be fabricated as detailed.  Substitutions will not be approved.


F.
High-Strength Bolted Connections (Amendments to the Specification for Structural Joints):



1.
In Item 3(b) of the specification, change the second sentence to read “Burrs shall be removed.”.



2.
In Item 3(c) of the specification, delete the last two sentences, and add the following sentence:  “Flame cut surfaces shall be ground smooth.”.



3.
In Item 7(b)(1) of the specification, add the following to the last sentence:  “, except that oversize holes shall not be used in connections with galvanized faying surfaces.”.



4.
In Item 7(b)(2) of the specification, add the following to the last sentence:  “, except that short slotted holes shall not be used in connections with galvanized faying surfaces when the force on the joint is in a direction other than normal to the axis of the slot.”.



5.
In Item 7(b)(3) of the specification, add the following to the last sentence:  “, except that long slotted holes shall not be used in connections with galvanized faying surfaces when the force on the joint is in a direction other than normal to the axis of the slot.”.



6.
Change Item 7(c)(3) of the specification to read as follows:  “All fully-tensioned high-strength bolts shall have a hardened washer under the element (nut or bolt head) turned in tightening, regardless of the method of tightening.”



7.
In Item 8(b) of the specification, change the first sentence to read:  “A tension measuring device shall be required at all work sites where fully-tensioned high-strength bolts are being installed.”.



8.
In Item 8(c) of the specification, delete the second and third sentences and add the following sentence:  “ The snug-tight condition is defined as the tightness attained by either a few impacts of an impact wrench or the full effort of a worker with an ordinary spud wrench that brings the connected plies into firm contact.”



9.
Change the last sentence in Item 8(c) to read “Unless otherwise required in the Specifications, bolts required to be fully-tensioned shall be  identified on the Drawings.  All other bolts need only be tightened to the snug tight condition.”



10.
In Item 9(b) of the specification, delete “Arbitration” from the heading.  Also change the first paragraph to read:  “When high-strength bolts have been installed by any of the tightening methods in Item 8(d), the following inspection procedure shall be used.”.



11.
In Item 9(c) of the specification, delete “arbitration” from the last sentence.



12.
In Item 9 of the specification, the inspection of bolt tightening shall be as specified under Item 9(b).  Furnish the calibration device and the inspection torque wrench, and make them available, upon request, to representatives of the State or designated inspection laboratory during the entire period when steel is being fabricated and erected.  The inspection torque wrench shall be capable of indicating that the job inspecting torque has been reached by a second method in addition to direct observation of the wrench dial.  The inspection wrench calibration and the bolt tightening inspection shall be performed by the Contractor, and shall be witnessed by a representative of the Director or the designated inspection laboratory.


G.
Design, Fabrication and Erection (Amendments to the AISC Specification):



1.
In Item A6. of the specification, change “American Welding Society” to “American Welding Society (Latest Adoption Date)”.  Delete the date from all referenced AWS Codes.



2.
In Item J1.8. of the specification, change the last sentence to read:  “Weld access holes and beam copes in other shapes shall be ground smooth, but need not be inspected by dye penetrant or magnetic particle methods.”.



3.
In Item J1.12 of the specification, delete “or with A307 bolts” from the second paragraph.



4.
In Item J2. of the specification, change the introductory sentence to read:  “All provisions of the American Welding Society Structural Welding Code-Steel, AWS D1.1, except Sections 2.3.2.4, 2.5, 8.13.1 and 9, apply to work performed under this Specification.”.



5.
In Item J3.2.c of the specification, change the first sentence to two sentences as follows:  “Oversized holes are permitted in any or all plys of slip-critical connections, except those with galvanized faying surfaces.  Oversized holes shall not be used in slip-critical connections with galvanized faying surfaces, or in bearing-type connections.”.



6.
In Item J3.2.d. of the specification, change the second sentence to two sentences as follows:  “Short-slotted holes are permitted without regard to direction of loading in slip-critical connections, except those with galvanized faying surfaces.  The length of the slot shall be normal to the direction of the load in slip-critical connections with galvanized faying surfaces and in bearing-type connections.”.



7.
In Item J3.2.e of the specification, change the second sentence to two sentences as follows:  “Long-slotted holes are permitted without regard to direction of loading in slip-critical connections, except those with galvanized faying surfaces.  The length of the slot shall be normal to the direction of the load in slip-critical connections with galvanized faying surfaces and in bearing-type connections.”.



8.
In Item M2.2. of the specification, delete the first two paragraphs.



9.
In Item M2.5. of the specification, change the second sentence of the fifth paragraph to read:  “Burrs shall be removed.”.



10.
Delete Item M4.5. of the specification in its entirety.



11.
In Item M5.4. of the specification, delete “Slip-critical” from the heading and delete “slip-critical” from the first sentence.


H.
Fabrication and Erection (Amendments to the AISC Code):



1.
In Item 4.1. of the code, delete the last sentence of the first paragraph.



2.
In Item 5.1. of the code, change the first paragraph to read: “Contract Drawings are not considered released for construction. Orders for materials may be placed only after approval of erection drawings or written approval of the Director.”

1.06
SUBMITTALS


A.
Shop Drawings:  Submit shop drawings for all structural steel required by this Contract.  Machine-duplicated copies of Contract Drawings will not be accepted as shop drawings.  Shop drawings shall be standard 24 by 36 inch size sheets, except that erection drawings may be larger.  The margin line shall be drawn a minimum of 1/2 inch from edge of sheet.  The title block shall be placed in the lower right hand corner of the drawing, and shall contain the fabricator’s name, address, and telephone number.  Failure to submit legible drawings of required size will be cause for their disapproval without review.  If the drawings are not prepared by a detailer under the direct control of the fabricator, the fabricator shall stamp each drawing and initial or sign the stamp to certify review and approval of the drawings, and conformance with the fabricator’s shop practice and capability.



1.
Include the following in the initial submission:




a.
Drawings of proposed job standards for shop and field connections, including standard and special connections, complying with the requirements.




b.
Erection drawings indicating sizes, weights, and locations of all structural members.




c.
Anchor bolt and base plate plans.



2.
Do not submit detail drawings, other than for anchor bolts and base plates, until after approval of the job standards and the erection drawings.



3.
All shop drawings shall be checked by the detailer before submission.  Failure to submit checked shop drawings will be cause for their disapproval without review.



4.
Changes initiated by the detailer or fabricator to previously reviewed shop drawings shall be resubmitted.


5.
Include the following in subsequent submissions:




a.
Index sheets and revised erection drawings to which erection marks have been added.




b.
Detail drawings of all structural members.



6.
Indicate all required shop and field welds by Standard AWS Welding Symbols in accordance with AWS A2.4.



7.
Indicate shop painting requirements.



8.
When shop drawings are marked “Approved as Noted”, promptly resubmit copies of corrected shop drawings for formal approval and record.



9.
Contract Drawings are not considered released for construction. Orders for materials may be placed only after approval of erection drawings or written approval of the Director.
USE PARAGRAPH BELOW WITH EPD REQUIREMENT WHEN PROJECT ESTIMATE IS $1M OR MORE.
B. 
Submit an Environmental Product Declaration (EPD) from the manufacturer for steel within this specification section, if available. A statement of the contractor’s good faith effort to obtain the EPD shall be provided if not available.

1. Manufacturer-provided EPDs must be Product Specific Type III (Third-Party Reviewed), in adherence with ISO 14025 Environmental labels and declarations, ISO 14044 Environmental management – Life cycle assessment, and ISO 21930 Core rules for environmental product declarations of construction products and services.

C.
Product Data:



1.
Shop Paint:  Manufacturer’s name and printed product literature, including storage and application instructions.


D.
Quality Control Submittals:



1.
Test Reports:  Submit test reports no later than the end of the week covered by the reports.  Submit copy of each test report required under Quality Assurance Article.


2.
Certificates:  Certificates required under Quality Assurance Article.


3.
Fabricator’s Qualifications Data:



a.
Firm’s name, business address and telephone number.




b.
Summary of their quality control programs.


4.
Erector’s Qualifications Data:



a.
Firm’s name, business address and telephone number.




b.
Summary of their quality control programs.



5.
Welder’s Qualifications Data:




a.
Name of each person who will be performing the Work and their employer’s name, business address and telephone number.




b.
Copy of AWS certification for type of welding required.
USE PARAGRAPH BELOW IF PROJECT IS INTENDED FOR LEED CERTIFICATION.


E.
LEED Design Submittals:



1.
MR Credit 4.1 and MR Credit 4.2:  Identify manufacturer’s name, the percentage of post-consumer recycled content by weight, the pre-consumer recycled content by weight, and the cost of the product.


2.
MR Credit 5.1 and MR Credit 5.2:  Identify source, cost, and the fraction by weight that is considered regional.
1.07
QUALITY ASSURANCE


A.
Test Reports:  



a.
Steel Manufacturer’s Mill Test Reports:  Covering physical and chemical tests, for all main material.



b.
Bolt Manufacturer’s Test Reports:   Covering physical and chemical tests, for each lot of high strength bolts supplied.


B.
Certification:  Affidavit by the structural steel manufacturer certifying that structural steel items meet the contract requirements.



1.
Submit evidence of steel material compliance with this Specification.  Evidence shall consist of certification of source of material, copies of purchase orders and manufacturer's certifications.  For stock material, submit copies of latest mill or purchase orders for material replacement.
USE SUBPARAGRAPH BELOW FOR PROJECTS OVER $100,000.  SEE PARAGRAPH 1.07 C. BELOW.



a.
Documentation to confirm compliance with General Conditions Article 25.4 Domestic Steel.
USE PARAGRAPH BELOW FOR PROJECTS OVER $100,000.  PARAGRAPH IS TAKEN FROM ARTICLE 25.4 OF THE GENERAL CONDITIONS.

C.
The Contractor agrees, that if the value of this contract exceeds $100,000 all structural steel, reinforcing steel and other major steel items to be incorporated in the Work of this Contract shall be produced and made in whole or substantial part in the United States, its territories or possessions.

D.
Qualifications:


1.
Fabricator’s Qualifications:  The fabricator of the structural steel shall be regularly engaged in the fabrication of structural steel for a minimum of 5 years, and shall be subject to the approval of the Director. 
a. AISC Quality Certified Fabricators (latest list issued) are approved.



2.
Erector’s Qualifications:  The structural steel erector shall be regularly engaged in the erection of structural steel for a minimum of 5 years, and shall be subject to the approval of the Director.



3.
Welders’ Qualifications:  Welding shall be performed only by welders, welding operators, and tackers who have been qualified by tests as prescribed in the AWS Code to perform the type of welding required.

Welders shall be certified for each type weld and position before fabrication.

E.
Do not deviate from the requirements of the Contract Documents except where an option is specifically mentioned.  The Director, however, may accept deviations proposed by the Contractor when it is deemed in the best interest of the State and if the deviations are consistent with sound and accepted engineering practice.  Requests for deviations shall be made prior to the submission of shop drawings to preclude delay in the expeditious preparation and approval of the required shop drawings.  In addition, design calculations or other data may be required to establish conformity of such deviations with the applicable Standards.


F.
Galvanizing:  Stamp galvanized items with galvanizer’s name, weight of coating, and applicable ASTM number.

USE PARAGRAPH BELOW WHEN REQUIRED BY PROJECT, CHECK WITH STRUCTURAL DESIGNER. 

G.
Pre-Fabrication Meeting:  A minimum of 14 days prior to the initial submission of shop drawings, a meeting will be held at the Site for the purpose of reviewing the Contract Documents, and discussing the requirements and procedures for submittals and for the Work.  The meeting will be conducted by the Director’s Representative.  The Contractor and the fabricator’s project coordinator and certified welding inspector must attend the meeting.  The Director’s Representative and a representative of OGS D&C Structural Engineering will also attend.

1.08
INSPECTION


A.
Quality Control Inspection:  Maintain Quality Control (QC) inspection during the fabrication and erection of structural steel.



1.
Submit for approval a summary of the QC programs of the proposed fabricator and erector, including a list of their QC personnel and respective duties.  Failure to obtain approval of the QC programs will result in rejection of the proposed fabricator and erector. AISC Quality Certified Fabricators submit copy of QC Certificate (Submission of QC program summary is waived).

IN SUBPARAGRAPH BELOW CHECK WITH DIVISION OF CONSTRUCTION FOR NUMBER AND NAMES OF INDEPENDENT TESTING LABORATORIES CURRENTLY UNDER CONTRACT FOR STRUCTURAL STEEL INSPECTION.


2.
At least one of the fabricator’s and one of the erector’s QC personnel shall be an American Welding Society Certified Welding Inspector (CWI).  If the fabricator and/or the erector find it necessary to temporarily employ an independent CWI, they shall not utilize Atlantic Testing Laboratories (under contract to the State) for structural steel inspection.



3.
The fabricator’s CWI shall make minimum QC inspections as follows and shall prepare daily reports of such inspections:




a.
At the start of fabrication to review welder qualifications, welding procedure specifications and qualifications, welding equipment and consumables, structural steel identification and tracking procedures and to perform all other CWI duties appropriate to start up of the specific project.




b.
Periodically during the preparation and fit up of material for groove welding.




c.
At all times that full penetration groove welding is being performed.




d.
As necessary to ensure that all welding related requirements of this section are being complied with.




e.
Minimum QC inspection time by the CWI shall be one-half day every other day that any welding related structural steel fabrication is being performed.



4.
The erector’s CWI shall make minimum QC inspections as follows, and shall prepare daily reports of such inspections:




a.
Prior to commencement of field welding operations to review welder qualifications, welding procedure specifications and qualifications, welding equipment and consumables and to perform all other CWI duties appropriate to start up of field welding for the specific project.




b.
Periodically during fit-up of material for full penetration groove welds.




c.
At all times that full penetration groove welding is being performed.




d.
As necessary to ensure that all welding related requirements of this section are being complied with.




e.
Minimum QC inspection time shall be one-half day on at least three separate days for every week that any structural steel field welding is being performed.  This minimum time may be reduced if, in the opinion of the Director’s Representative, such reduction is appropriate.


B.
Quality Assurance (QA) inspection of structural steel fabrication and field welding and high-strength bolting may be made at the discretion of the Director.  The qualification of welding procedures, welders, and tackers will be covered by such QA inspection.  Representatives of the Director and/or designated inspection laboratory shall be given free and easy access to fabrication shop and field at all times that work is in progress.  QA inspections will be made without cost to the Contractor.



1.
If QA inspection is made by the State, it shall not relieve the Contractor, fabricator, and erector of responsibility for their own QC programs.



2.
When QA inspection is made by the State, schedule and perform the Work as required to minimize the cost to the State for QA inspection.  When failure to schedule and perform the Work, or to coordinate with the QA inspectors, results in excessive QA inspection costs, the State will backcharge such excess cost to the Contractor.



3.
When non-destructive testing, Radiographic Testing (RT) or Ultrasonic Testing (UT), is required by the contract documents, it shall be performed by the State or its designated inspection laboratory, at the State’s expense.



4.
When QA inspection is made by the State, send 3 additional copies of required material certifications and mill test reports to the designated inspection laboratory, or to OGS Design & Construction, Division of Construction when no inspection laboratory has been designated.



5.
Keep copies of the results of welder qualification test on file and make them available to the QA inspector upon request.



6.
Do not ship structural steel, except anchor bolts and base plates, from the fabricating shop prior to QA inspection and approval by the State or designated inspection laboratory, unless such inspection is waived by the Director.  A waiver of prior QA inspection and approval shall not reduce the Contractor’s responsibility to provide structural steel in conformance with the Contract Documents.

1.09
WELDING PROCESSES


A.
Use only shielded metal arc, submerged arc, gas metal arc, or flux cored arc welding.

1.10
WELDING PROCEDURE QUALIFICATION


A.
Shielded metal arc, submerged arc, gas metal arc, or flux cored arc welding procedures which conform to the provisions of the AWS Code shall be considered to be prequalified.


B.
The welding procedures requiring qualification shall conform to the requirements of AWS D1.1.
1.11
DELIVERY, STORAGE, AND HANDLING


A.
Deliver anchor bolts and other devices which are to be embedded in cast-in-place concrete or masonry construction, for anchorage of structural steel, one week prior to the start of that Work, unless otherwise required.


B.
Receiving Shop Paint:  Receive paint in original, unopened containers bearing paint manufacturer’s printed label.



1.
Label shall show manufacturer’s name, trade name of paint, Federal Specification compliance (if applicable), shelf life, and date of manufacture.


C.
Protection:



1.
Upon delivery to the site, promptly cover and protect steel items (which are not required to receive shop paint) from rusting.



2.
Store shop paint in accordance with paint manufacturer’s printed instructions.

1.12
ENVIRONMENTAL REQUIREMENTS FOR SHOP PAINTING


A.
Comply with the following conditions for the application of paint unless otherwise stated in the paint manufacturer’s printed directions.



1.
Minimum ambient, steel surface, and paint temperatures:  40 degrees F.



2.
Maximum steel surface temperature:  100 degrees F.



3.
Maximum relative humidity:  85 percent.



4.
Surface of steel:  Dry.

USE ARTICLE BELOW WITH TRUSS FABRICATION, CHECK WITH STRUCTURAL DESIGNER.
1.13
MINIMUM SHOP FACILITIES FOR TRUSS FABRICATION


A.
The fabricator shall possess sufficient lifting capacity, physical plant and equipment for the fabrication and painting of structural steel trusses including a minimum of two overhead cranes.  The cranes in each working area shall have a combined rated capacity equal to the lifting weight of the heaviest assembly fabricated for shipment.  A preliminary physical plant inspection will be made by the Director’s Representative to verify compliance.


B.
Spreader beams, or multiple cranes, shall be provided for lifting long slender assemblies to prevent overstress and distortion from handling.


C.
The fabricator shall be responsible for the proper preparation of groove joints to be welded in the field.  The joints shall be prepared and assembled in the shop to insure that proper joint alignment and fit up is present at each joint when the correct camber is in the assembled pieces.


D.
When truss members of any cross section are to be spliced by welding in the field, a detailed welding procedure shall be submitted to the Director for approval.  The procedure shall be detailed on shop drawings, submitted and approved prior to the fabrication of structural steel.  The detailed field welding procedure shall include the method of supporting members during welding.  All field welded splices shall be subject to non-destructive testing, Radiographic Testing (RT), or Ultrasonic Testing (UT), as determined by the Director.  Field splice locations, when specifically shown on contract documents, shall not be relocated nor shall splices be added without written approval of the Director.

PART 2   PRODUCTS

2.01
MATERIALS


A.
Wide Flange Structural Steel:  ASTM A 992, except as specified or shown otherwise.

B.
M and S-Shapes, Channels and Angles:  ASTM A 36 or ASTM A 572, Grade 50.

C.
HP-Shapes:  ASTM A 572, Grade50.


D.
Steel for Anchor Bolts, Tie Rods, Sag Rods, and other Detail Material Not Proportioned for Calculated Stress:  ASTM A 36; or ASTM A 675, Grade 70.


E.
Steel for Shims and Fillers:  ASTM A 569.


F.
Exterior Lintels:  ASTM A 36, galvanized.


E.
High-Strength Threaded Fasteners (High-Strength Bolts):  ASTM A 325 heavy hexagon structural bolts, nuts, and hardened washers.


G.
Steel Pipe:  ASTM A 53, Type E or S, Grade B.

CHECK PARAGRAPH BELOW WITH STRUCTURAL DESIGNER.  EDIT AS REQUIRED.  COLUMN LOAD TABLES ARE BASED ON ASTM A 500, GRADE B (Fy=46 ksi) TUBING.  FOR LIGHTLY LOADED OR LONG COLUMNS, ASTM A 501 (Fy=36 ksi) TUBING MAY BE ACCEPTABLE.

H.
Steel Hollow Structural Sections (Round, Square, or Rectangular):  ASTM A 500, Grade B; or ASTM A 500, Grade C.

I.
Weld Filler Metal:



1.
General:  Weld filler metal shall be in accordance with Table 4.1.1 of the AWS Code, except as follows:




a.
Only electrode and flux combinations complying with AWS Classifications F7AX-EXXX or F7AX-EXXX-a, (a = B2, Ni1, Ni2, Ni3 or W), shall be used for submerged arc welding.




b.
Only electrode and shielding gas combinations complying with AWS Classifications E 7XT-1 or E 7XT-5 shall be used for flux cored arc welding.



2.
Weld filler metal for shielded metal arc, submerged arc, gas metal arc, and flux cored arc welding which conforms to AWS Specifications A5.1 or A5.5 shall be considered to be prequalified.

“STUDS” IN PARAGRAPH BELOW ARE ROUND, HEADED, SHEAR CONNECTORS WELDED TO STRUCTURAL STEEL MEMBERS.

J.
Steel Studs:  Automatic arc welded studs complying with Section 7 of the AWS Code.


K.
Cold Galvanizing Compound:  Single component compound giving 93 percent pure zinc in the dried film, and meeting the requirements of DOD-P-21035A (NAVY).


L.
Shop Paint (General):  Steel primer selected from the following:



1.
TNEMEC 10-99 (Red), 10-99G (Green) or 10-1009 (Gray).



2.
Rust-Oleum 769.



3.
Valspar 13-R-53.



4.
Sherwin-Williams “Kromik”.


M.
Shop Paint for Galvanized Steel:  FS TT-P-641, Type II.


N.
Shop Paint for Steel to receive Sprayed-On Fireproofing:  Primer paint, if any, recommended by the manufacturer of the fireproofing material approved for use on this Project.


O.
Shop Paint for Exterior Structural Steel (High-Ratio Water Based Inorganic Zinc Silicate):  Steel primer selected from the following:



1.
Sherwin Williams ZincClad X1.


2.
Carboline Carbozinc 18 WB.

P.
Bedding Mortar:



1.
Cement Grout:  Portland cement complying with ASTM C 150, Type I or III, and clean uniformly graded natural sand complying with ASTM C 404, size No. 2; mixed at a ratio (by volume) of 1.0 part cement to 3.0 parts sand, with only the minimum amount of water required for placement and hydration.

USE SUBPARAGRAPH ABOVE AND/OR BELOW AS REQUIRED.  CHECK WITH STRUCTURAL DESIGNER.  WHEN USING SHRINK RESISTANT GROUT USE FERROUS TYPE IN SUBPARAGRAPH BELOW UNLESS OTHERWISE DIRECTED BY STRUCTURAL DESIGNER.


2.
Shrink-Resistant Grout (Ferrous):  Factory-packaged, non-catalyzed, ferrous aggregate mortar grouting compound selected from the following:




a.
Embeco 636 by Master Builders, 23700 Chagrin Blvd., Cleveland, OH 44122 (800) 227-3350.




b.
Ferrolith G-NC by Sonneborn, Chemrex, Inc., 57-46 Flushing Ave., Maspeth, NY 11378, (800) 433-9517.




c.
Ferro-Grout by L&M Construction Chemicals, 14851 Calhoun Rd., Omaha, NB 68152, (800) 362-3331.




d.
Vibra-Foil by A.C. Horn, Inc., Tamm Industries, 7405 Production Dr., Mentor, OH 44060, (800) 862-2667.

USE SUBPARAGRAPH BELOW ONLY WHEN DIRECTED BY STRUCTURAL DESIGNER,


3.
Shrink-Resistant Grout (Non-Staining):  Factory-packaged, non-ferrous mortar grouting compound selected from the following:




a.
Masterflow 713 by Master Builders, 23700 Chagrin Blvd., Cleveland, OH 44122 (800) 227-3350.




b.
Sonogrout by Sonneborn, Chemrex, Inc., 57-46 Flushing Ave., Maspeth, NY 11378, (800) 433-9517.




c.
Five Star Grout by Five Star Products, Inc., 425 Stillson Rd., Fairfield, CT 06430, (800) 243-2206.




d.
Crystex by L&M Construction Chemicals, 14851 Calhoun Rd., Omaha, NB 68152, (800) 362-3331.




e.
Non-Corrosive, Non-Shrink Grout by A.C. Horn, Inc., Tamm Industries, 7405 Production Dr., Mentor, OH 44060, (800) 862-2667.

2.02
FABRICATION


A.
Do not commence fabrication until the fabricator has been approved and the fabrication schedule has been coordinated with the designated Quality Assurance inspection agency (independent inspection laboratory or the State).



1.
Give the Director’s Representative one week advance notice of the commencement of fabrication.


B.
Progress shop fabrication from “Approved” or “Approved as Noted” detail drawings only.



1.
When detail drawings are “Approved as Noted”, progress fabrication in strict accordance with notes thereon.



2.
Fabrication progressed from “DISAPPROVED” or “RETURNED FOR CORRECTION” detail drawings will be rejected.  The contractor shall have no claim against the State for any costs or delays due to rejection of items fabricated from “DISAPPROVED” or “RETURNED FOR CORRECTION” detail drawings.


C.
Finish column ends at base plates and at load carrying cap plates to a true plane square to the column, with a maximum American National Standards Institute surface roughness value of 500 microinches.


D.
Pipe and Tube Columns:  Cap columns with a closure plate shop welded to the top of the columns to exclude water and foreign material from entering the column.


E.
Loose Lintels:  Loose lintels bearing on masonry or concrete shall have a minimum end bearing length of 6 inches at each end, unless otherwise noted.


F.
Make provision for connections of other Work, including all cutting and punching of structural members where required by the Drawings, or for which information is furnished prior to approval of the shop drawings.


G.
Weld and inspect steel studs in accordance with Section 7 of the AWS Code.


H.
Remove extension bars or run-off plates upon the completion and cooling of groove welds.  Grind the ends of the welds smooth and flush with the edges of the abutting parts.


I.
Remove tack welds not incorporated into the final weld, and temporary welds.  Grind affected surfaces smooth and flush.


J.
Detail all fillet welded joints so as to permit the welding electrode or wire to be positioned at a minimum angle of 30 degrees from the face of any material upon which weld metal is to be deposited.


K.
Prepare material in accordance with Section 3 of the AWS Code.  Do not use gas or air carbon-arc cutting to cut or enlarge bolt holes.

2.03
GALVANIZING


A.
Unless otherwise specified or noted, items indicated to be galvanized shall receive a zinc coating by the hot-dip process, after fabrication, complying with the following:



1.
ASTM A 123 for plain and fabricated material.



2.
ASTM A 153 for iron and steel hardware.

2.04
SHOP PAINTING


A.
Thoroughly clean all structural steel.  Remove oil, grease, and similar contaminants in accordance with SSPC SP-1 “Solvent Cleaning”.  Remove loose mill scale, loose rust, weld slag and spatter, and other detrimental material in accordance with SSPC SP-2 “Hand Tool Cleaning”, SSPC SP-3 “Power Tool Cleaning”, SSPC SP-6“ Commercial Blast Clean” or SSPC SP-7 “Brush-Off Blast Cleaning, or SSPC SP-10 “Near-White Blast Cleaning”.
USE SUBPARAGRAPH BELOW WHEN STEEL IS RECEIVING SPRAYED-ON FIREPROOFING.


1.
Thoroughly clean structural steel receiving sprayed-on fireproofing in accordance with recommendations of the manufacturer of the fireproofing material approved for use on this Project.



2.
Provide SSPC SP-1 “Solvent Cleaning” to all Hollow Structural Section (HSS) surfaces to be painted.



3.
Provide SSPC SP-10 “Near-White Blast Cleaning” to all steel members to receive High-Ratio Water Based Inorganic Zinc Silicate Paint.
USE PARAGRAPH BELOW WHEN STEEL IS RECEIVING SPRAYED-ON FIREPROOFING.

B.
Coordinate shop paint to be applied on steel receiving sprayed-on fireproofing with the manufacturer of the fireproofing material approved for use on this Project.


C.
Galvanized Items:



1.
Galvanized items which are to be finish painted under Section 099101 shall be rinsed in hot alkali or in an acid solution and then in clear water.



2.
Welded and abraded galvanized surfaces shall be wire brushed and repaired with a coating of cold galvanizing compound applied in accordance with compound manufacturer’s instructions.


D.
Exterior Exposed Steel:


1.
Provide surface profile range of 1.5 -2.0 mils for structural steel to receive High-Ratio Water Based Inorganic Zinc Silicate.



2.
Apply a stripe coat of High-Ratio Water Based Inorganic Zinc Silicate paint on all horizontal and vertical edges of exterior steel members, 2.0 mil dry film thickness.


E.
Apply one coat of shop paint to all steel surfaces except as follows:



1.
Do not paint steel members designated “NP” on the Drawings.



2.
Paint steel surfaces scheduled to be painted that are inaccessible after assembly, except surfaces in contact, with two coats of shop paint before assembly.



3.
Do not paint steel surfaces to be field welded, contact surfaces of high-strength bolted slip-critical connections, steel to be encased in cast-in-place concrete, steel receiving sprayed-on fireproofing , and the top flange of beams and girders in composite construction.



4.
Do not paint galvanized items which are not to be finish painted under Section 099101.



5.
Apply two shop coats of High-Ratio Water Based Inorganic Zinc Silicate to all exterior steel member surfaces.


F.
Apply paint and compound to the following minimum thickness per coat:



1.
Shop Paint (General):  4.0 mils wet film.



2.
Shop Paint for Galvanized Steel:  3.0 mils wet film.



3.
Cold Galvanizing Compound:  2.0 mils dry film.



4.
Shop Paint for Steel to receive Sprayed-On Fireproofing:  Follow manufacturer’s recommendations.



5.
Shop Paint (Water-Based Zinc Silicate): 3.0 mils dry film.

PART 3   EXECUTION

3.01
ERECTION


A.
Erect steel in accordance with the AISC Specification, the AISC Code, the AWS Code and the Specification for Structural Joints, except as otherwise specified.


B.
Prepare and place shrink-resistant grout in accordance with grout manufacturer’s printed instructions.



1.
Comply with manufacturer’s instructions for preparation of surfaces in contact with the grout, and for curing and protection of the grout.


C.
Install and inspect steel studs in accordance with Section 7 of the AWS Code.


D.
Remove extension bars and run-off plates upon the completion and cooling of groove welds.  Grind the ends of the welds smooth and flush with the edges of the abutting parts.


E.
Remove tack welds not incorporated into the final weld, and temporary welds.  Grind affected surfaces smooth and flush.


F.
Delete Paragraph M2.2 of the AISC Specification.  Prepare material in conformance with Section 3 of the AWS Code.  Do not use gas or air carbon-arc cutting to cut or enlarge bolt hole.


G.
Do not make corrections or alterations to fabricated steel without prior written approval by the Director’s Representative.

3.02
SCHEDULE OF GALVANIZED STRUCTURAL STEEL


A.
In addition to members indicated on the Drawings, hot-dip galvanize structural steel members as indicated below:



1.
All exterior exposed steel.



2.
All loose lintels in exterior walls.



3.
All framing supporting refrigerator/freezer equipment.



4.
Nuts, washers and the top 12 inches of exterior anchor bolts.


B.
Two shop coats of High-Ratio Water Based Inorganic Zinc Silicate paint may be substituted in lieu of hot-dip galvanizing.

END OF SECTION

Updated 06/29/2023

Printed 06/29/2023
051200 - 16
Project No.


