D&C  JRC:lmm

SECTION 224713
DRINKING FOUNTAINS

PART 1   GENERAL

1.01
RELATED WORK SPECIFIED ELSEWHERE


A.
Fixture Carrier Supports:  Section 224200.

1.02
SUBMITTALS


A.
Product Data:  Manufacturer’s catalog sheets, specifications and installation instructions for each type drinking fountain.


B.
Contract Closeout Submittals:



1.
Operation and Maintenance Data:  Deliver 2 copies, covering the installed products, to the Director’s Representative.

1.03
QUALITY ASSURANCE


A.
Regulatory Requirements:



1.
Comply with applicable requirements of FS WW-P-541 unless otherwise specified.



2.
Comply with the Federal Safe Water Drinking Act of 1986, and the Federal Lead Contamination Control Act of 1988.



3.
Materials and installations designated as handicapped accessible shall conform with the following:




a.
ANSI A117.1 - Buildings and Facilities - Providing Accessibility and Usability for Physically Handicapped People.




b.
The Americans with Disabilities Act Accessibility Guidelines for Buildings and Facilities (ADAAG), (Appendix A to 28 CFR Part 36).




c.
The Uniform Federal Accessibility Standards (UFAS), (Appendix A to 41 CFR Part 101-19.6).

USE ARTICLE BELOW ONLY WITH FROST PROOF DRINKING FOUNTAINS.
1.04
MAINTENANCE


A.
Special Tools:  Deliver the following to the Director’s Representative:



1.
Tools for Vandal Resistant Fasteners:  One for each type and size.

PART 2   PRODUCTS
2.01
DRINKING FOUNTAINS


A.
Type:  Wall mounted, factory assembled, complete with trap, shut off valve and wall hanger.

CHANGE MATERIAL IN PARAGRAPH BELOW TO ENAMELED CAST IRON OR VITREOUS CHINA IF REQUIRED.

B.
Body:  Polished or satin finished stainless steel, 18 gauge or heavier; with rounded corners, anti-splash back, and receptor contoured to eliminate splashing.


C.
Features:  Self closing supply valve, automatic stream regulator, two stream mound building projector and removable brass strainer plate.



1.
All exposed brass trim polished and chrome plated.

USE PARAGRAPH BELOW WHEN FROSTPROOFING IS REQUIRED.

D.
Frost Proof Assembly:  The supply valve body and trap assembly for the drinking fountain shall be housed in a steel plumbing cabinet and arranged for mounting on the opposite (heated) side of the building wall.  All piping extending from the plumbing cabinet to the drinking fountain shall automatically drain to the heated side of the wall.



1.
Attach projector and valve handle with vandal resistant fasteners.



2.
Use vandal resistant fasteners where exposed on the drinking fountain and plumbing cabinet.

MODIFY PARAGRAPH BELOW IF OTHER CONFIGURATIONS ARE REQUIRED.  CHECK WITH DESIGNER.

E.
Configuration:  Approximately 12 inches square with a full skirt of sufficient depth to conceal the principal operating parts and with a security cover fastened to the underside of the fountain body.


F.
Fixture Hanger:  Steel, designed to mount fixture to fixture support, as furnished by drinking fountain manufacturer.  See Section 224200.

2.02
HANDICAPPED ACCESSIBLE DRINKING FOUNTAINS


A.
Type:  Wall mounted, factory assembled.  Complete with trap, shut off valve and wall hanger.


B.
Body:  Polished or satin finished stainless steel, 18 gauge or heavier; with rounded corners and receptor contoured to eliminate splashing.


C.
Features:  Self closing supply valve, automatic stream regulator, two stream mound building projector and removable brass strainer plate.



1.
All exposed brass trim polished and chrome plated.

MODIFY PARAGRAPH BELOW IF OTHER CONFIGURATIONS ARE REQUIRED.  CHECK WITH DESIGNER.

D.
Configuration:  Approximately 12 inches wide and 20 inches front to back with full skirt of sufficient depth to conceal the principal operating parts and with a security cover fastened to the underside of the fountain body.


E.
Operators:  Front push bar or push bar on each side.



1.
Maximum Activation Force:  5 ft lbs.


F.
Projector Clearance:  Projector to back wall distance must be 12 inches or greater.


G.
Fixture Hanger:  Steel, designed to mount fixture to fixture support, as furnished by drinking fountain manufacturer.  See Section 224200.

2.03 FASTENERS

A.
Vandal Resistant Fasteners:  Torx head with center pin.

PART 3   EXECUTION

3.01
INSTALLATION


A.
Install the Work of this section in accordance with the manufacturer’s printed installation instructions.


B.
Standard Fixture Mounting Height (unless otherwise indicated on the Drawings):  Distance finished floor to rim.



1.
Adult Usage:  40 inches.

USE SUBPARAGRAPH BELOW ONLY WHEN DIRECTED BY DESIGNER.


2.
Child Usage:  29 inches.

USE PARAGRAPH ABOVE AND/OR BELOW.  EDIT AS REQUIRED.

C.
Handicapped Accessible Fixture Mounting Height:  Maximum distance finished floor to spout outlet.



1.
Handicapped Accessible Usage: 36 inches.

REMEMBER TO INCLUDE DRAWING REFERENCED IN SUBPARAGRAPH BELOW.  INSERT AT END OF SECTION.


2.
Refer to Standard Drawing No. 93/S3012, bound herein, for special clearance requirements required for handicapped fixtures.

3.02
CLEANING, FLUSHING AND ADJUSTMENT


A.
Clean and polish fixture and trim.


B.
Flush piping; clean strainers and trap.


C.
Adjust for proper delivery.

END OF SECTION


[image: image1.wmf]
Updated 07/08/09

Printed 4/15/2015
224713 - 2
Project No. 


_1164093128.bin

