D&C  WB/DMD:gp


SECTION 233418
CENTRIFUGAL WALL EXHAUSTERS

PART 1   GENERAL

EDIT ARTICLE BELOW AS REQUIRED.
1.01
RELATED WORK SPECIFIED ELSEWHERE


A.
Wiring for Motors and Motor Controllers:  Section 260523.


B.
Motors and Motor Controllers:  Section 260221.

1.02
SUBMITTALS


A.
Product Data:  Catalog sheets, specifications, standard schematic drawings, and installation instructions for each fan specified.

1.03
QUALITY ASSURANCE


A.
Regulatory Requirements:



1.
Exhausters, with wheels 12 inches in size and larger, shall be licensed to bear the AMCA seal.



2.
Electrical components shall be UL listed.

PART 2   PRODUCTS

2.01
WALL EXHAUSTER


A.
General Design:  Quiet operating, direct drive centrifugal fan, with an aluminum, backward curved, non-overloading wheel, dynamically balanced with motor and enclosed in a fan housing of spun aluminum.


B.
Components:



1.
Fan Housing:  Fabricated from heavy gage spun aluminum, with flanges for anchoring to exterior wall surfaces.  Power assembly shall be isolated from housing, with stainless steel springs, or equivalent means as approved.  Fan housing shall be easily removable for access to motor and servicing.



2.
Motor:  Speed or speeds of motors shall be as noted on drawings.  Single phase fractional horse power motors shall be of the capacitor, split phase or shaded pole type, with ball or lifetime lubricated bearings and built-in thermal overload protection.



3.
Shutters:  Aluminum self-opening type.  Frame and blades shall be fabricated of aluminum; bearings shall be bronze or nylon.  Damper blades shall be coupled together with tie rods at each end and edges of blades shall be felted.



4.
Bird Guards:  Fabricate from heavy gage polished steel wire on maximum 1/2-inch spacings and install in discharge openings of fan assembly.



5.
Disconnect Switch:  Factory mounted, UL approved, moisture tight, unfused disconnect switch, located inside the motor compartment next to the motor terminal box.


C.
Exhausters, bird guards and shutters shall be the product of the same manufacturer.


D.
Exposed fastening devices shall be aluminum or stainless steel.

2.02
SEALANT


A.
Acrylic Type:  FS TT-S-00230.

PART 3   EXECUTION

3.01
INSTALLATION


A.
Set exhauster wall mounting flanges in a heavy bead of acrylic sealant.


B.
Secure units in accordance with manufacturer’s printed instructions and approved shop drawings.

END OF SECTION

Updated 07/08/09

Printed 4/15/2015
233418- 2
Project No. 


