D&C  JC/LZ:ss


SECTION 330111
REPAIRING STEEL WATER STORAGE TANK

THIS SECTION BASED ON AWWA D-101.  CONSULT D-101 WHEN EDITING.
PART 1   GENERAL

1.01
RELATED WORK SPECIFIED ELSEWHERE


A.
Disinfection:  Section 331300.


B.
Painting:  Section 099701.

1.02
QUALITY ASSURANCE


A.
Welders Qualifications:



1.
Skilled in the type of welding required by this project.



2.
Certified in accordance with the applicable provisions of the ASME Code.


B.
Reference Standard:  Comply with specification AWWA D-100 for the Work of this section.  Maintain a copy of this reference standard at the Site at all times.

1.03
SUBMITTALS


A.
Shop Drawings:  Show items to be replaced.  Indicate size, weight, and spacing of steel members.

PART 2   PRODUCTS

2.01
MATERIALS


A.
Replacement Items:  Same size, strength, and dimensions as the original equipment.


B.
Shop paint all items before delivery to the Site.

PART 3   EXECUTION

3.01
REPAIRS


A.
Weld leaky seams and rivets on inside of tank.


B.
Seal weld interior lap joints of roof plates above maximum water line to provide a paintable surface.


C.
Repair all holes resulting from structural changes as required to insure a watertight tank.

LIST ADDITIONAL REPAIRS ABOVE.

D.
Make additional repairs as listed below:



1.


3.02
LEAKAGE TEST


A.
Fill tank to maximum water level.  Inspect for leaks after 48 hours.


B.
Repair leaks (if any).


C.
Repeat leakage tests when directed.

END OF SECTION

Updated 07/08/09

Printed 4/14/2015
330111 - 2
Project No. 


