SECTION 330507

HORIZONTAL DIRECTIONAL DRILLING

PART 1   GENERAL

1.01	RELATED WORK SPECIFIED ELSEWHERE

A.	Geotechnical Data:  Section 003132.

B.	Underground Utility Locator Service:  Section 023313.

C.	Traffic Maintenance and Protection:  Section 015526.

D.	Earthwork:  Section 310000.

E.	Dewatering:  Section 312319.

F.	Plastic Water Pipe: Section 331102.

G.	Plastic Drainage Pipe (Sanitary): Section 333104.

1.02	DESCRIPTION

A.	The Work of this Section consists of operations, equipment, methods and materials necessary to install horizontal directional drilling (HDD) of High-Density Polyethylene (HDPE-PE) Pressure pipe.

1.03	SUBMITTALS

A.	Submittals Package: Submit the following items specified below the same time as a package:

1.	Written Drilling Procedure.

2.	Quality Control Submittal.

B.	Written Drilling Procedure:  Describes in detail proposed method and entire operation but not limited to the following:

1.	Size, capacity and arrangement of equipment, drawn to scale.

2.	Location and size of drilling and receiving pits.

3.	Dewatering and methods of removing spoils material.

4.	Method of installing detection wire and pipe.

5.	Type, location and method of installing locator station.

6.	Method of fusion pipe segment and type of equipment.

7.	Type of cutting head.

8.	Method of monitoring and controlling line and grade.

9.	Detection of surface movement.

10.	Bentonite drilling mud for information only.

11.	Products information, material specifications, and handling

procedures.

12.	Material safety data sheet and special precautions required.

13.	Method of mixing and application.

C.	Quality Control Submittals:

1.	Contractor’s Qualifications Data:

a.	Firm name, address, and phone number.

b.	Period of time that the firm has been in the business of performing horizontal directional drilling.

c.	Names and addresses of 5 similar projects completed by the firm.  Include the name and phone number of contact person.

2.	Field Supervisor Qualifications Data:

a.	Name of the person supervising the horizontal directional drilling.

b.	Period of time that the person has performed/supervised horizontal directional drilling.

b.	Names and addresses of three similar projects that the person has worked on during the past three years.

D.	Contract Closeout Submittals

1.	Reproducible as-built drawings showing dimensions, accurate locations, and depth of burial at 100 ft intervals.  Marked-up contract drawings will not be acceptable.

2.	Issue a written report at the conclusion of the installation phase, stating whether or not specifications and approved manufacturer’s installation recommendations.

3.	Furnish a signed report to the Director’s Representative.

E.	The submittal will not relieve the Contractor of complete responsibility to 	the successful performance of the intended installation procedure.

1.04	QUALITY ASSURANCE

A.	Qualifications:

1.	Contractor:  The firm performing the Work of this Section shall have been regularly engaged in performing horizontal directional drilling for a minimum of 10 years, and shall have completed 5 similar projects of size and complexity over the last 5 years.

2.	Field Supervisor:  The person supervising the Work of this Section shall have been regularly engaged in performing horizontal directional drilling for a minimum of 5 years and shall have supervised 3 similar projects of size and complexity over the last 3 years.

B.	Pre-Installation Conference: Before the work is scheduled to commence, a conference will be called by the Director’s Representative at the Site for the purpose of reviewing the Contract Documents and discussing requirements for the Work.  The conference shall be attended by related trade Contractors (if any), their qualified installers and Field Supervision.

1.05	PROJECT CONDITIONS

A.	Complete HDD so as not to interfere with, interrupt, or endanger surface and activity thereon.

B.	Do not use HDD in rock stratum or subsoil consisting of boulders and underground obstructions that impede the process.

C.	Follow applicable ordinances, codes, statutes, rules, and regulations of State of New York, and applicable regulations of Federal Government, OSHA 29CFR 1926, and applicable criteria of ANSI A10.16-1995 (R2001), “Safety Requirements for Tunnels, Shafts, and Caissons.”

PART 2   PRODUCTS

2.01	MATERIALS

A.	Pipe and Fittings:

1.	Water Pipe:  Refer to Section 331102.

2.	Sanitary Sewer Pipe:  Refer to Section 333104.

B.	Joining Method:

1.	Water Pipe:  Refer to Section 331102.

2.	Sanitary Sewer Pipe:  Refer to Section 333104.

3.	When joining HDPE pipe at ends of directional drilling runs fusion bond to adjacent pipe section using butt fusion.

4.	Mechanical couplings are not permitted for joining of directional drilled pipe sections.

C.	Drilling Fluid:

1.	Bentonite drilling mud compatible with environment.

2.	Waste oil or environmentally non-compatible polymers cannot be part of composition.

D.	Detection Wire: TW, THW, THWN, or HMWPE insulated copper, 10 gage or

thicker wire.

E.	Locator Station.

1.	Underground, Flush Mounted:

a.	Tube minimum 15 inches long with minimum inside diameter of 2-1/2-inches made of non-corrosive material, schedule 40 PVC, HDPE, or equal.

b.	Factory attached cast iron or high-impact plastic collar with ribs to prevent rotation when removing locking lid after locator station is set in concrete.

c.	Light blue cast iron or high-impact plastic locking lid that will withstand AASHTO H-20 traffic loads and ultra-violet rays.

d.	Mark locking lid to identify pipeline with permanent identification such as P.S. Locator.

e.	Terminal block made of high dielectric material which is made of phenolic resin, plastic, micarta, Lexan or Bakelite for each locator station.  Terminal block furnished with two 3/16-inch threaded studs, nuts, and washers made of nickel-plated brass.

f.	Manufacturers: C.P. Test Services, Inc., Model Mini; Handly, Industries, Model T2IS2.

2.	Manhole Mounted:

a.	Waterproof enclosure made from cast aluminum, galvanized steel, high-impact plastic, Lexan, Gyrlyn, or equal.

b.	Light blue schedule 40 PVC pipe or schedule 40 galvanized steel with outside diameter of at least 3/4-inch to mount enclosure.

c.	Use similar materials for pipe and enclosure to fasten enclosure onto pipe following manufacturer's instructions.

d.	Manufacturers: Cott Manufacturing Company, Model Finklet or Finkplate, 2 leads; Gerome Manufacturing Company, Inc., Model Testox Series 300, 2 leads.

PART 3   EXECUTION

3.01	PREPARATION

A.	Underground Utilities:  Refer to Section 023313.

1.	Locate and mark-out existing, underground utilities along directional drill path.  Perform Level A locator service in all project areas.

2.	Determine vertical orientation and depths of utility lines along directional drill path.

B.	Pit Preparation:

1.	Excavate pits following contract documents are as specified by the Director’s Representative.

2.	Dewater pits as required and as directed.

3.02	OPERATION

A.	General.

1.	Determine drilling length and equipment pull strength for type of soil encountered.

2.	Provide method to control line and grade.

a.	Provide and maintain instrumentation that accurately locates pilot hole.

b.	Drill pilot hole along path following Drawings to these tolerances:

1)	Vertical alignment plus or minus 0.5 foot. Vertical path of pilot hole must not establish new high points not shown on Drawings.

2)	Horizontal alignment plus or minus 1.0 foot.

c.	Include electronic monitoring of horizontal and vertical drilling head location.  Obtain accuracy range within 1 inch of actual position of pipeline.  Record position readings at maximum of 10-foot intervals.

d.	At completion of pilot hole drilling, furnish tabulations of horizontal and vertical alignment to Engineer.

3.	When water is encountered.:

a.	Provide and maintain dewatering system of sufficient capacity to remove water.   Refer to Section 312319.

b.	Keep excavation free of water until backfill operation is in progress.

c.	Perform dewatering in manner that removal of soils particles are held to minimum.

d.	Dewater into sediment trap.

4.	Maintain close observation to detect settlement or displacement of surface and adjacent facilities.

a.	Notify Director’s Representative immediately if settlement or displacement is detected.

b.	Maintain safe conditions and prevent damage.

B.	Drilling Operation.

1.	Drilling Fluids.

a.	Maintain drilling fluid in bore hole to increase stability of surrounding soil and reduce drag on pulled pipe.

b.	Dispose of drilling fluid and other spoils at location following laws, ordinances, rules, and regulations of local jurisdiction.

c.	Transport excess fluids and other spoils to disposal site, at no additional cost to the contract.

d.	Minimize drilling fluid at locations other than entry and exit points. Immediately clean up any drilling fluids that inadvertently surface.

e.	Provide clean water for drilling, at no cost to the contract, and as directed by the Director’s Representative.

2.	Pilot Hole Drilling.

a.	Angle entry hole so that the curvature of pilot hole does nto exceed allowable radius of HDPE pipe.

b.	Be able to make turn of up to 90 degrees and maintain curvature not to exceed allowable bending radius of HDPE pipe.

c.	Alignment adjustment and restarts:

1)	Follow pipeline alignment on Drawings within tolerances specified herein.  Before adjustments, notify Director’s Representative for approval.

2)	Notify Director’s Representative when forward motion of operation is stopped by an obstruction.

a)	Abandon in place with drilling fluid, unless

Directors’ Representative directs otherwise.

b)	Upon the Director’s Representative’s approval, attempt second installation at approved location or excavate at point of difficulty and install HDPE pipe by trench methods specified in Section 310000.

3.	Withdrawals, abandonments, and restarts are at no additional costs to the Contract when HDD is provided as an option of installation of pipe.

4.	Exercise caution including, but not limited to, locating utilities, drilling downholes (test pits) to observe drill stems or reamer assembly to clear other existing utilities at locations following drawings.

5.	Keep the number of boring pits to a minimum.

3.03	INSTALLATION

A.	Installing HDPE Pipe

1.	Provide a swivel to reaming assembly and pull section of pipe to minimize torsional stress on pull section after drilling pilot hole.

2.	Hold reaming diameter to 1.5 times outside diameter of HDPE pipe being installed.

3.	Protect pull section as it proceeds during pull back so it moves freely and is not damaged.

4.	Pull detection wire along with HDPE pipe. Extend wire into locator station at each end of the HDPE pipe.

5.	When connecting to adjacent pulled or non-pulled section of HDPE pipe, allow pull section of pipe to extend past termination point. Make tie-ins the next day after pull back of HDPE pipe.

6.	Test pit pipe installation to verify horizontal and vertical alignment at Director’s Representative’s direction.

a.	One test pit every 500 feet along length of pipeline, if not within environmentally sensitive and/or protected area.

b.	Director’s Representative may order additional test pits for each test pit that reveals pipeline installation is not in compliance with the Contract Documents at no additional cost to the Contract.

7.	Replace portions of pipeline not in compliance with the Contract Documents at Director’s Representatives direction and at no cost to the Contract.

B.	Installing Locator Station

1.	Location Stations:

a.	When HDPE pipe is connected to another type of pipe material, continue detector wire over connecting pipe, so locator station is installed out of paved area.

b.	In areas scheduled to be improved identify and protect station locations immediately after installation.

1)	Space 3 stakes equally around the station.

2)	Extend at least 4 feet above existing grade.

2.	Detection Wire.

a.	Install detection wire without splices unless specified on the plans.

b.	Terminate detection wire inside locator box using proper sized crimp type connection on wire ends.

c.	Neatly coil slack wire in test station below terminal board.

d.	Locate wires on top and along HDPE pipe.

e.	Allow adequate slack and support to protect wires from damage during backfilling operations.

f.	Test each detection wire for continuity after backfill is completed.

1)	If test for continuity is negative, repair or replace at Director’s Representative’s direction.

2)	After continuity is verified, connect each detection wire to terminal block in locator station.

3.04	FIELD QUALITY CONTROL

A.	Perform field testing of HDPE pipe following Section 331102 for water and 331104 for sanitary sewer.

3.05	MAINTENANCE AND RESTORATION

A.	Restore grades to original levels where settlement or damage due to performance of the Work has occurred.  Correct conditions contributing to settlement.  Remove and replace improperly placed or poorly compacted fill materials.

B.	Restore pavements, walks, curbs, lawns, and other surface features damaged during performance of the Work to match the appearance and performance of existing corresponding features as closely as practicable.

C.	Topsoil and seed or sod damaged lawn areas.

END OF SECTION