D&C  IK:dh/dja


SECTION 331101
WATER UTILITY DISTRIBUTION PIPING
USE FOR MECHANICAL JOINT OR PUSH-ON JOINT PIPE.  SEE SECTION 211101 FOR FLANGED JOINTS.
PART 1   GENERAL

1.01
RELATED WORK SPECIFIED ELSEWHERE

EDIT PARAGRAPH BELOW FOR CONCRETE SECTION USED.

A.
Concrete For Thrust Blocks:  Section 033000 or 033001.


B.
Earthwork:  Section 310000.


C.
Water Utility Distribution Valves:  Section 331216.


D.
Disinfection:  Section 331300.

1.02
SUBMITTALS


A.
Product Data:  Manufacturer’s specifications including dimensions and coatings.


B.
Quality Control Submittals:  Statement of compliance with ANSI/AWWA Specifications.

PART 2   PRODUCTS

2.01
ACCEPTABLE MANUFACTURERS


A.
U.S. Pipe

1101 East Pearl Street

Burlington, New Jersey 08016

(609)387-6122


B.
American Pipe

1614-0 Union Valley Road, Suite 304

West Milford, New Jersey 07480

(973)853-4288

C.
EBAA Iron Sales, Inc.

P.O. Box 857

Eastland, TX  76448

(800) 433-1716

www.ebaa.com

2.02
DUCTILE IRON PIPE

EDIT BELOW TO SUIT PROJECT.  CONSULT ANSI/AWWA TABLES TO VERIFY PIPE THICKNESS CLASS FOR THE PARTICULAR DEPTH OF COVER AND LAYING CONDITIONS.

A.
Centrifugally cast, in accordance with ANSI/AWWA C151/A21.51.



1.
Working Pressure:  100 psi.



2.
Thickness Class:  Under 6 inch - 51; 6 inch and larger - 50.



3.
Restrained joints:  Boltless integral restraining system rated for a working pressure of 350 psi in accordance with the performance requirements of ANSI/AWWA C111/A21.1.




a.
Field LOK 350 by U.S. Pipe



b.
Flex-Ring by American Pipe


4.
Laying Lengths:  18 or 20 feet.


B.
Coating and Lining:



1.
Outside Coating:  Bituminous enamel, minimum thickness 1 mil.



2.
Inside Lining:  Cement mortar; ANSI/AWWA C104/A21.4.

2.03
FITTINGS

SELECT ONE OF THE NEXT TWO PARAGRAPHS.

A.
Ductile Iron (3 Inch – 48 Inches):  ANSI/AWWA C110/A21.10.


B.
Compact Ductile Iron Fittings (3 Inch – 64 Inches):  ANSI/AWWA C153/A21.53.


C.
Joints:  Match pipe furnished.


D.
Coating and Lining:



1.
Outside Coating:  Bituminous enamel, minimum thickness 1 mil.



2.
Inside Lining:  Cement mortar; ANSI/AWWA C104/A21.4.

2.04
FLEXIBLE EXPANSION JOINTS

SELECT ONE OF THE TWO PARAGRAPHS BELOW DEPENDING ON THE INDICATED DESIGN REQUIREMENT.

A.
Single ball flexible expansion joint designed for protection against bending moments.



1.
EBAA Iron Sales, Inc.

B.
Double ball flexible expansion joint designed for protection against shear and ground movement.



1.
EBAA Iron Sales, Inc.

C.
Construction:



1.
Manufactured of 65-45-12 ductile iron conforming to the material requirements of ASTM A536 and ANSI/AWWA C153/A21.53.



2.
Working Pressure:  350 psi for flexible joints 3 inch through 24 inch in size; 250 psi for flexible joints 30 inch and over in size.



3.
Expansion joint designed and cast as an integral part of a ball and socket type flexible joint; 4 inch minimum expansion capability.



4.
Each ball and socket capable of at least 15 degrees deflection.



5.
Coating and Lining:




a.
Outside Coating:  Coat tar epoxy, minimum thickness 5 mils.




b.
Inside Lining and Seal Contact Surfaces:  NSF approved fusion-bonded epoxy conforming to the material requirements of and tested in accordance with ANSI/AWWA C213.



6.
Joints (Mechanical Joint or Flanged Ends):  Match joints of pipe furnished.



7.
Pressure tested against its own restraint at rated working pressure.

PART 3   EXECUTION

3.01
INSPECTION


A.
Inspect pipe and fittings prior to installation to preclude installation of defective materials.

3.02
INSTALLATION


A.
General:  Unless otherwise shown, or specified, install the Work of this Section in accordance with ANSI/AWWA Standard C600 and the manufacturer’s printed instructions.


B.
Laying Pipe:



1.
Lay pipe to line and grade with joints close and even.  Excavate adequate bell holes to facilitate joint assembly and to permit a uniform bearing on undisturbed earth for the pipe barrel.  Unless otherwise noted minimum depth of pipe shall be 4’-6” measured from the top of the pipe to the finished or existing grade, whichever is lower.



2.
Keep the trench free from water.  Do not lay or test pipe in a wet trench.



3.
Lay water pipe on a continuously rising grade from low points to high points at service lines, hydrants or air valves.



4.
Construct concrete thrust blocks behind bends, tees, caps and plugs, as shown on the drawings.  Cast concrete against undisturbed earth and place support so it will not interfere with making joints.



5.
Use clamps, tie-rods, lugged pipe, etc., for anchorage when required and as approved.


C.
Push-on Joints:  Make joints with a rubber ring and sterile lubricant.  The materials used shall be free of water, oil, tar, grease or other foreign substances.


D.
Mechanical Joints:  Conform strictly to the manufacturer’s instructions with particular reference to gland alignment and the tightening of the bolts.


E.
Cutting:  Cut pipe at right angles to the axis with sharp tools.  Prepare ends for proper connections.  Do not lay cut pipe within three lengths of a bend or the end of a line without written approval.


F.
Protecting Pipe:



1.
Keep pipe clean from all sediment, debris, packing material and other foreign material.



2.
Close all open ends of pipes and fittings securely with removable plugs at end of each work day, during storms, and when the Work is left at any time.

3.03
PRESSURE AND LEAKAGE TESTS


A.
Before backfilling, fill pipe with water to expel all air.  Conduct as directed concurrent pressure and leakage tests for two hours at 1-1/2 times the specified working pressure.  Maximum variation in test pressures shall not exceed plus or minus 5 psi.



1.
Test Procedures:  ANSI/AWWA C600, Section 5.

MAKE SURE THE WORKING PRESSURE OF PIPE IS SPECIFIED.

B.
Pipe installations will be rejected when the additional water required to maintain pressure during the test period, exceeds the allowable leakage in the following formula.




L = SD X the square root of P




148,000




in which:




L = allowable leakage in gallons per hour




S = length of pipe line tested, in feet




D = nominal diameter of pipe, in inches




P = average test pressure during the leakage test, psi (gage)


C.
All pressure and leakage tests shall be conducted in the presence of the Director’s Representative.


D.
Locate and repair or replace all pipe and fittings showing visible leaks.  Repeat Pressure and Leakage Tests as specified.

3.04
DISINFECTION


A.
Disinfect pipe and fittings in accordance with Section 331300 after completion of pressure and leakage tests.

3.05
CONNECTIONS


A.
When other connecting pipe or other connecting structures have not yet been installed, lay pipe to a point where directed and plug or cap the end.  Identify the terminal point with a stake extending above ground, marked to indicate size and service.  Provide temporary thrust restraint as directed.

END OF SECTION

Updated 03/08/2010
Printed 04/14/2015
331101 - 1
Project No. 


