D&C  WAF:amp


SECTION 331220
STREET WASHERS

PART 1   GENERAL

1.01
RELATED WORK SPECIFIED ELSEWHERE

EDIT AS REQUIRED.

A.
Earthwork:  Section 310000.


B.
Concrete:  Section 033000.

1.02
SUBMITTALS


A.
Product Data:  Manufacturer's catalog cuts, specifications and installation instructions.

PART 2   PRODUCTS

2.01
STREET WASHERS


A.
Provide frost-proof type with an automatic drip valve at the bottom of the barrel.  Washers shall be capable of withstanding a working pressure of 150 psi and be complete with keys and wrenches as required.  Working parts shall be of bronze and the box shall be of cast iron with a locking cover.  Street washers shall be equal to Murdock Model M6100 or Eclipse No. 36.

MAKE SURE INLET SIZE IS SHOWN ON THE DRAWINGS.

B.
Coarse Aggregate:  Broken stone, maximum size 2 inches.

PART 3   EXECUTION

3.01
INSTALLATION


A.
Unless otherwise shown, set inlet at such depth as to provide 4'-6" cover over pipe inlet.


B.
Place two cubic feet of broken stone around the waste outlet.

DELETE BELOW IF NOT REQUIRED.

C.
Set street washer box in concrete pad.

END OF SECTION

Updated 07/08/09

Printed 4/14/2015
331220 - 1
Project No. 


