D&C  JC/WRS:lmm


SECTION 333103
DRAINAGE PIPE (SANITARY)
THIS SECTION COVERS CONCRETE AND CAST/DUCTILE IRON PIPE 24 INCHES AND UNDER IN SIZE FOR GRAVITY SEWER APPLICATIONS.
PART 1   GENERAL

1.01
RELATED WORK SPECIFIED ELSEWHERE


A.
Concrete Cradles:  Section 033000.


B.
Earthwork:  Section 310000.


C.
Underdrain Filter Material:  Section 310000.


D.
Rock Removal:  Section 312316.


E.
Manholes:  Section 334913.

1.02
SUBMITTALS


A.
Product Data:  Manufacturer’s specifications including dimensions and strength for each type of pipe.

USE PARAGRAPH BELOW WITH EPD REQUIREMENT WHEN PROJECT ESTIMATE IS $1M OR MORE.
B. 
Submit an Environmental Product Declaration (EPD) from the manufacturer for concrete this specification section, if available. A statement of the contractor’s good faith effort to obtain the EPD shall be provided if not available.

1. Manufacturer-provided EPDs must be Product Specific Type III (Third-Party Reviewed), in adherence with ISO 14025 Environmental labels and declarations, ISO 14044 Environmental management – Life cycle assessment, and ISO 21930 Core rules for environmental product declarations of construction products and services.

PART 2   PRODUCTS

2.01
CONCRETE PIPE


A.
Furnish pipe of the strength given in the table below.  Use standard strength pipe unless extra strength is indicated.

EDIT TABLE BELOW TO SUIT PROJECT.
	PIPE STRENGTH

(Lbs/Lin Foot - ASTM Three-Edge Bearing Method)

	PIPE SIZE (INCHES) 
	STANDARD STRENGTH
	EXTRA STRENGTH

	4
	1500
	2000

	6
	1500
	2400

	8
	1500
	2400

	10
	1600
	2400

	12
	1800
	2600

	15
	2000
	2900

	18
	2200
	3300

	21
	2400
	3850

	24
	2600
	4400



B.
Pipe and Fittings:  ASTM C 14


C.
Joints and Gaskets:  ASTM C 443.

2.02
POROUS CONCRETE PIPE


A.
Pipe Classification:  ASTM C 654.  Comply fully with this standard except as modified below.


B.
External Load Crushing Requirements:  Standard Strength.


C.
Tongue-and-Groove Joints.


D.
Infiltration Requirement:  Not less than 2 gpm per inch of internal diameter per lineal foot of pipe.


E.
Acceptable Manufacturer:  Walker Poroswall Pipe Co., 110 Bergen Turnpike, Little Ferry, NJ  07643, (201) 440-2542.

2.03
IRON PIPE AND FITTINGS

GRAY CAST IRON (AWWA C-106 & C-108) IS NO LONGER MANUFACTURED.  FOR GRAVITY SEWER APPLICATIONS, USE EITHER SERVICE WEIGHT CAST IRON OR CLASS 50 DUCTILE IRON.  USE SERVICE WEIGHT CAST IRON WHERE TRENCH LOADING IS MINIMAL AND WHERE MANY FITTINGS ARE REQUIRED.  CAST IRON FITTINGS ARE LESS THAN 1/2 THE COST OF DUCTILE IRON FITTINGS.  USE DUCTILE IRON WHERE TRENCH LOADING OR VIBRATION DUE TO IMPACT ARE FACTORS, OR WHERE PIPE RUN IS STRAIGHT WITH MINIMUM FITTINGS.  USE SECTION 02511 FOR PRESSURE APPLICATIONS.

A.
Ductile Iron Class 50:  ANSI/ASTM A 746; coat pipe and fittings inside and outside with an asphaltic coating at least 1 mil in thickness.

CHOOSE EITHER PARAGRAPH ABOVE OR PARAGRAPH BELOW.

B.
Service Weight Cast Iron:  ASTM A 74; coat pipe and fittings inside and outside with an asphaltic coating at least 1 mil in thickness.

PART 3   EXECUTION

3.01
INSPECTION


A.
Examine all pipe and fittings before installation.  Remove defective pipe and fittings from the Site.


B.
Do not backfill until inspected by the Director’s Representative.

3.02
INSTALLATION


A.
Laying Pipe:



1.
Lay pipe to indicated line and grade with a firm uniform bearing throughout its length.



2.
Lay pipe with a uniform pitch between high and low points.



3.
Position bells upstream.



4.
Provide sufficient clearance at each bell or coupling to allow uniform bearing along the pipe barrel.  Fill excess excavation with suitable material and tamp.


B.
Joints:



1.
Wipe inside of sockets and outside of pipe to be jointed, clean and dry.



2.
Install rubber gaskets in accordance with the manufacturer’s specifications.


C.
Connections:



1.
Make connection to existing sewers by springing two or more joints and inserting a “Y” fitting.  Remake all damaged existing joints.



2.
Make connections to existing manholes by cutting into the floor or bench of the manhole and forming a new channel.



3.
If the pipe, manholes or other structures with which connection is to be made has not yet been installed, install the pipe to a point directed by the Director’s Representative and plug or cap the end in a satisfactory manner.


D.
Porous Concrete Pipe:



1.
Install pipe in accordance with the manufacturer’s recommendations and as indicated on the drawings.



2.
Graded stone or gravel aggregate conforming to at least 85 percent passing through a 3/8 inch screen and 100 percent retained on a No. 35 screen shall be used for bedding and backfill to the depth shown on the drawings.

3.03
LEAKAGE TESTS


A.
Test the first 100 feet of sewer construction for leakage before backfilling or laying additional pipe.



1.
Fill the sewer with water and maintain a head two feet above the highest section of work being tested.  Measure the quantity of leakage.



2.
When the sewer being tested is constructed in water bearing soil, the leakage test may, at the discretion of the Director’s Representative, be made by measuring the quantity of infiltration into the sewer.



3.
Allow the concrete pipe to become saturated for a period of 72 hours prior to measuring leakage.


B.
Maximum Allowable Leakage or Infiltration:



1.
Concrete Pipe:  35 gallons per 24 hours per inch of pipe diameter per 1000 feet of sanitary sewer being tested; 50 gallons per 24 hours per inch of pipe diameter per 1000 feet of storm sewer being tested.



2.
Ductile Iron and Cast Iron Pipe:  25 gallons per 24 hours per inch of pipe diameter per 1000 feet of both sanitary and storm sewer being tested.


C.
Perform, as directed, additional leakage tests and a final test.

END OF SECTION

Updated 06/29/2023

Printed 6/29/2023
333103 - 4
Project No. 


