D&C  WAF:amp


SECTION 334101
REINFORCED CONCRETE PIPE (STORM DRAINAGE)
PART 1   GENERAL

1.01
RELATED WORK SPECIFIED ELSEWHERE


A.
Earthwork:  Section 310000.


B.
Rock Removal:  Section 312316.

1.02
SUBMITTALS


A.
Product Data:  Manufacturer's data including dimensions and strength information.

USE PARAGRAPH BELOW WITH EPD REQUIREMENT WHEN PROJECT ESTIMATE IS $1M OR MORE.
B. 
Submit an Environmental Product Declaration (EPD) from the manufacturer for concrete this specification section, if available. A statement of the contractor’s good faith effort to obtain the EPD shall be provided if not available.

1. Manufacturer-provided EPDs must be Product Specific Type III (Third-Party Reviewed), in adherence with ISO 14025 Environmental labels and declarations, ISO 14044 Environmental management – Life cycle assessment, and ISO 21930 Core rules for environmental product declarations of construction products and services.

PART 2   PRODUCTS

2.01
MATERIAL

FILL IN BLANK BELOW AND INCLUDE IN UNIT PRICE SCHEDULE.  CHOOSE CLASS TO MEET PROJECT'S STRENGTH REQUIREMENTS. WORD PROCESSING PERSON:  DELETE UNDERLINE BEFORE ADDING INFORMATION.

A.
Reinforced Concrete Pipe:  DOT Section 706-02, Class     .

PART 3   EXECUTION

3.01
INSPECTION


A.
Inspect all pipe and fittings before laying in the trench.  Remove defective pipe and fittings from the site.


B.
Do not backfill until inspection by the Director's Representative.

3.02
INSTALLATION


A.
Laying Pipe:  Lay pipe to line and grade with a firm uniform bearing for the entire length of the pipe.  Excavate sufficient clearance at each bell hole to make the joint.  Fill excess excavation with suitable material and tamp.


B.
Joints:  Manufacturer's standard unless indicated otherwise on the drawings.


C.
Connections:



1.
Make connections to existing sewers, by springing two or more joints and inserting a "Y" fitting.  Remake all damaged existing joints.



2.
Make connections to existing manholes by cutting into the floor or bench of the manhole and forming a new channel.



3.
If the pipe, manholes or other structures with which connections are to be made has not yet been installed, install the pipe to a point directed by the Director's Representative and plug or cap the end in a satisfactory manner.

3.03
LEAKAGE TESTS


A.
Prior to backfilling and laying additional pipe, test the first 100 feet of sewer construction for leakage.



1.
Fill the sewer with water and maintain a head two feet above the highest section of Work being tested.  Measure the quantity of leakage.  When the sewer being tested is constructed in water bearing soil, the leakage test may, at the discretion of the Director's Representative, be made by measuring the quantity of infiltration into the sewer.  The allowable leakage or infiltration shall not be exceeded.



2.
The rate of leakage or infiltration shall not exceed 50 gallons per 24 hours per inch pipe diameter per 1000 feet of sewer being tested.


B.
Additional leakage tests and a final test shall be performed as directed.

END OF SECTION

Updated 06/29/2023

Printed 6/29/2023
334101 - 2
Project No. 


