D&C  ACB:dja

SECTION 337119
ELECTRIC MANHOLES

PART 1   GENERAL

1.01
RELATED WORK SPECIFIED ELSEWHERE


A.
Earthwork:  Section 310000.


B.
Cast-In-Place Concrete:  Section 033000.

1.02
DEFINITIONS


A.
The words manhole, handhole and pullbox are synonymous.

1.03
SUBMITTALS


A.
Waiver of Submittals:  The "Waiver of Certain Submittal Requirements" in Section 013300 does not apply to the following products specified in this Section:



1.
Manholes.



2.
Manhole covers and frames.

USE PARAGRAPH BELOW WITH EPD REQUIREMENT WHEN PROJECT ESTIMATE IS $1M OR MORE.
B. 
Submit an Environmental Product Declaration (EPD) from the manufacturer for concrete this specification section, if available. A statement of the contractor’s good faith effort to obtain the EPD shall be provided if not available.
1. Manufacturer-provided EPDs must be Product Specific Type III (Third-Party Reviewed), in adherence with ISO 14025 Environmental labels and declarations, ISO 14044 Environmental management – Life cycle assessment, and ISO 21930 Core rules for environmental product declarations of construction products and services.


C.
Product Data:  Catalog sheets, specifications and installation instructions.


D.
Shop Drawings:  Show dimensions, reinforcing and construction details for manholes.

PART 2   PRODUCTS

2.01
MANHOLES


A.
Manholes may be precast or field constructed:



1.
Field Constructed Manholes:  Furnish manholes of dimensions as shown on the drawings.
USE STANDARD DETAILS ON THE DRAWINGS.


2.
Precast Manholes:  As manufactured by The Fort Miller Co., or Lakelands Pre-cast, Inc., having:




a.
Reinforcing meeting American Association State Highway Officials requirements for H-20 loading. Drawings shall bear the seal of a professional engineer licensed to practice in the State of New York.




b.
Minimum interior dimensions as shown on the drawings for field constructed manholes.




c.
Walls minimum 6 inches thick reinforced concrete.  Exception:





1)
Walls minimum 4-l/2 inches thick reinforced concrete for 30 x 30 inch manholes.




d.
Top slab minimum 7 inches thick reinforced concrete.  Exceptions:





1)
Top slab minimum 6 inches thick reinforced concrete for 4 x 4 foot manholes.





2)
Top slab not required for 30 x 30 inch manholes.




e.
Bottom slab minimum 6 inches thick reinforced concrete.  Exception:





1)
Bottom slab minimum 4 inches thick reinforced concrete for 30 x 30 inch manholes.




f.
Sealed joints.


B.
Equip manholes with a pulling hook opposite each conduit entrance.  Construct hook of 3/4 inch galvanized stock with 3 inch diameter eye and 8 inches for anchoring in manhole wall or use Pennsylvania Pulling Iron as manufactured by Pennsylvania Insert Corporation.

DO NOT INSTALL DRAINS (PARAGRAPH BELOW) IN MANHOLES, EXCEPT WHERE WATER TABLE IS SUITABLE TO ALLOW USE OF DRAIN SPECIFIED (WATER TABLE NOT ABOVE MANHOLE FLOOR).

C.
Provide a drain in center of manhole consisting of 30 inch length of 6 inch diameter vitrified sewer pipe extending downward under floor and filled with broken stone.

DO NOT INSTALL DRAINS (PARAGRAPH BELOW) IN MANHOLES, EXCEPT WHERE A CONNECTION TO STORM SEWER IS AVAILABLE.  IF PARAGRAPH BELOW IS USED COORDINATE WITH TEAM LEADER FOR STORM SEWER CONNECTION.

D.
Provide a cast iron drain pipe in side wall of manhole, consisting of 4 inch diameter heavy cast iron soil pipe extending 3 feet beyond outer surface of manhole wall.  Equip side drain pipe with perforated cover inside manhole.  Plug end of pipe outside of manhole and leave for future connection by others.


E.
Brick shall comply with the Specifications for Sewer Brick, Grade MS, ASTM C32.


F.
Mortar:  One part of Portland cement to 2 parts sand, mixed with water for proper consistency.


G.
Waterproofing for Bricked-Up Throat:  Single component, rubber reinforced asphalt elastomeric coating, ASTM D-4586 Type I and ASTM D-4479 Type I.
2.02
WATERTIGHT MANHOLE FRAMES AND COVERS


A.
Design of each shall be the same throughout the project unless otherwise specified or indicated on the drawings.


B.
Units shall meet AASHTO H20 wheel loading requirements.  Manufacture, workmanship and certified proof-load tests shall conform to AASHTO M306-89.



1.
Material:




a.
Cast iron:  ASTM A48, Class 30B or 35B.




b.
Delivered to the site free of any coatings, unless otherwise specified.



2.
Frames:




a.
Round, 6-1/2 inches high with a 27-inch clear opening.




b.
Minimum bearing area of the flange on the masonry:  645 sq. inches.




c.
Minimum weight:  156 lbs.



3.
Outer Lids:




a.
Round, approximately 1-1/2 inches thick at the perimeter bearing surface.




b.
Minimum one inch wide perimeter bearing surface.




c.
Unperforaced checkered surface design.




d.
Concealed type pick holes.




e.
The letter "P" 6 inches high cast in the outer lid for power manholes; the letter "S" 6 inches high for signal manholes.




f.
Minimum weight:  215 lbs.



4.
Inner Lids:




a.
Each equipped with two lift handles, a neoprene seating gasket, and a lock bar with a hasp or other means suitable for padlocking.




b.
Minimum total weight of lid and lock bar:  165 lbs.


C.
Acceptable Frames and Covers:  Pattern R1755-G1 by Neenah Foundry Company, P. O. Box 729, Neenah, WI  54957, (414) 729-3661; Pattern 6553 by Syracuse Casting Sales Corp., P. O. Box 190, South Bay Rd., Cicero, NY  13039, (315) 699-2601.

2.03
CABLE SUPPORT ASSEMBLIES


A.
Cable Support Assemblies (Steel):  A.B. Chance Co.'s 1225 rack, 1231 Series support arms, 1121 porcelain insulators, or McGraw-Edison's DU10B Series rack, DU9S Series support arms, DE12U porcelain insulators.


B.
Cable Support Assemblies (Nonmetallic):  Underground Devices Inc.'s CR36 rack, RA Series support arms.

C.
Cable Ties: Heavy-Duty Durable nylon construction with reinforced head and strap.

1.
Length as required.

2.
Minimum width .345 inches

3.
Minimum loop Tensile 175 lbs.

2.04
GROUNDING AND BONDING


A.
Rod Electrodes:  Copper clad (min. .010 jacket) ground rods minimum 5/8 inch diameter by 8'-0" long.


B.
Exothermic Type Weld:  Erico Products Inc.'s  Cadweld Process.


C.
Compression Connectors:  Amp Special Industries' Ampact Grounding System, Burdy Corp.'s Hyground System, or Thomas & Betts Corp.'s Grid and Ground Rod System.


D.
Grounding Electrode Conductors and Bonding Conductors:  Bare copper conductors.


E.
Hardware:  Silicon-bronze bolts, nuts, flat and lock washers, etc. as manufactured by Burndy Corp., Dossert Corp., or OZ/Gedney Co.

PART 3   EXECUTION

3.01
PREPARATION


A.
Dewater and remove debris from existing manholes used for the Work.


B.
Provide heavy blankets, plywood or other devices to protect existing cables and equipment from physical damage.

3.02
INSTALLATION


A.
Depth:  Install manholes at depth required to bring top of manhole covers 2 inches above finished grade in lawns, and flush with paved surfaces of walks, roads, or parking spaces.


B.
Bricked-Up Throat:  Mortar brick into place.  Set manhole frame with mortar.  Waterproof exterior of throat with minimum thickness of 3/32 inch elastic bituminous plastic cement coating.


C.
Cable Supports:  Install racks, support arms and insulators of size and number to provide one insulator (or equivalent space on nonmetallic support arms) on each cable support assembly for each conduit entering the manhole:



1.
New Manholes or Pullboxes:  Route cables around periphery of manholes (or pullbox).  Secure cables to cable support assemblies with cable ties. Equip manholes and pullboxes with number of cable support assemblies indicated below:




a.
Manholes:

1)
Where conduits penetrate 2 adjacent sides of a manhole, provide a minimum of 3 cable support assemblies.

2)
Where conduits penetrate 2 opposite sides of a manhole, provide a minimum of 3 cable support assemblies.

3)
Where conduits penetrate 3 sides of a manhole, provide a minimum of 3 cable support assemblies.

4)
Where conduits penetrate 4 sides of a manhole, provide a minimum of 6 cable support assemblies.




b.
Pullboxes:

1)
Where conduits penetrate 2 adjacent sides of a pullbox, provide a minimum of 2 cable support assemblies.

2)
Where conduits penetrate 2 opposite sides of a pullbox, provide a minimum of 1 cable support assemblies.

3)
Where conduits penetrate 3 sides of a pullbox, provide a minimum of 3 cable support assemblies.

4)
Where conduits penetrate 4 sides of a pullbox, provide a minimum of 4 cable support assemblies.



2.
Existing Manholes or Existing Pullboxes: Equip existing manholes (or pullboxes) with cable support assemblies as required to support new cables.  Route new cables around periphery of manhole.  Secure cables with cable ties to cable support assemblies. Equip manholes and pullboxes with number of cable support assemblies indicated in paragraphs “a and b” above to support new cables. 

INDICATE ON THE DRAWINGS, IF EXISTING UNRACKED CABLES ARE TO BE SET ON CABLE SUPPORT ASSEMBLIES.
a.
Set existing unracked cables on cable support assemblies where indicated on the drawings.  Secure cables with cable ties to cable support assemblies.


3.
Signal Manholes or Pullboxes:  In addition to cable support assemblies, provide across and spanning the support arms, troughs for support of each signal cable.  Troughs shall consist of lengths of 4 inch diameter Schedule 40 plastic conduit split lengthwise into halves.  Route cables around periphery of manhole.  Set trough on the support arms, lay in cable and secure with cable ties.


D.
Grounding and Bonding:



1.
New Manholes Containing Feeder Circuits Over 600 Volts:




a.
Install rod electrode in each manhole near a wall.  Install rod electrode thru floor into earth below manhole with 4 inches protruding for ground connection.




b.
Bond manhole cover frame, steel cable support assemblies and splices (lead sheath of splice or cable shields for non-lead type cables) to rod electrode with No. 6 AWG bare copper ground conductor.  




c.
Make connection to rod electrode with exothermic type weld or compression connectors.



2.
Existing Manholes Containing New Splices Over 600 Volts:




a.
Install a rod electrode in each manhole where new cable splices are required (existing rod electrodes may be utilized if available).  Install rod electrode thru floor into earth below manhole with 4 inches protruding for ground connection.




b.
Bond existing manhole cover frame, new and existing steel cable support assemblies and new splices (lead sheath of splice or cable shields for non-lead type cables) to rod electrode with No. 6 AWG bare copper ground conductor.




c.
Make connection to rod electrode with exothermic type weld or compression connectors.

END OF SECTION

THE REMAINDER OF THIS SECTION IS FOR INFORMATION ONLY; NOT TO BE INCLUDED IN PROJECT SPECIFICATIONS.

1.
Codes, Standards, and References applicable to manholes:


a.
National Electrical Code - Article 300.3 (C) (2) (e).


b.
National Electrical Safety Code - Section 323.

END OF INFORMATION
Updated 06/29/2023
Printed 06/29/2023
337119 - 5
Project No.

