D&C  FJS:gp


SECTION 337994
LIGHTNING PROTECTION SYSTEM FOR CHAIN LINK FENCE

THIS SECTION COVERS THE LIGHTNING PROTECTION SYSTEM USED ON CHAIN LINK FENCING FOR CORRECTIONAL FACILITIES IN LIGHTNING PRONE AREAS.
PART 1   GENERAL

1.01
REFERENCES


A.
Except as shown or specified otherwise, conform to the applicable requirements of UL 96A “Installation Requirements for Lightning Protection Systems” and NFPA 780 “Lightning Protection Code”.  Note:  UL Master Label will not be required.

1.02
SUBMITTALS


A.
Waiver of Submittals:  The “Waiver of Certain Submittal Requirements” in Section 013300 does not apply to this Section.


B.
Submittals Package:  Submit the product data, and the shop drawings specified below at the same time as a package.


C.
Product Data:  Catalog sheets, specifications and installation instructions.


D.
Shop Drawings:



1.
Scale drawings of the complete system as proposed to be installed.



2.
Size and location of all conductors.



3.
Methods of attachments.



4.
Location, size and types of ground electrodes.



5.
Schematic diagram (standard diagrams will not be accepted).


E.
Samples:  One of each product if requested.  Samples will be returned and if approved, may be used in the Work.


F.
Contract Closeout Submittals:



1.
Test Report:  System acceptance test report.

PART 2  PRODUCTS

2.01
MATERIALS


A.
Acceptable Manufacturers:



1.
Heary Bros., Springville, NY.



2.
Independent Protection Co., Goshen, IN.


B.
Copper:  Grade ordinarily required for commercial electrical Work, generally designated as being 98 percent conductivity when annealed.


C.
Cable (Main Size):



1.
Copper weighing not less than 375 lbs. per 1000 feet.



2.
The size of any wire in the conductor not less than No. 15 AWG.



3.
Minimum cross sectional area of 115,000 cir. mil.


D.
Connections and Splices:  Suitable configuration and type for the intended application and of the same material as the conductor.


E.
Rod Electrodes:  Solid copper or copper-clad ground rods, 3/4 inch minimum diameter, 10’-0” long.


F.
Surge Arresters:  Joslyn’s J9200-7 thru 12 Series, to suit system secondary characteristics.


G.
Attachments:  Suitable configuration for the intended application and of the same material as the conductor.  Nails, screws, or bolts employed to secure the fasteners shall be of the same material as the fasteners or of material that is as resistant to corrosion as that of the fasteners.  (Galvanized or plated steel nails, screws or bolts are not acceptable).


H.
Exothermic Type Weld:  Continental Industries Inc.’s Thermoweld, or Erico Products Ind.’s Cadweld Process.

PART 3   EXECUTION

SHOW DETAILS ON THE DRAWINGS.  THE DETAILS ARE AVAILABLE IN THE OFFICE ON A REFERENCE DRAWING.
3.01
INSTALLATION


A.
Conductor Bends:  No bend in a conductor shall have a radius less than 8 inches.  The angle of any turn shall not be less than 90 degrees.  Conductors shall maintain a horizontal or downward course.


B.
Connections and Splices:  Use connector fitting on conductors at end-to-end, tee or Y splices of type designed for the particular application and attached to withstand a pull test of 200 pounds.


C.
Grounding:



1.
Provide rod electrode for each main conductor.



2.
Install electrode so that top of electrode is not less than 2 feet below grade.



3.
Thoroughly tamp earth against the conductor and electrodes the full distance to which they are extended.



4.
The nearest electrode shall not be less than 2 feet from fence or wall.



5.
Where electrode consists of a driven rod, the length of the electrode shall be permanently marked upon it at the top.



6.
If the grounding system is found to have a resistance exceeding the parameters of the referenced codes, drive additional rod electrodes or provide other approved grounding electrodes to obtain the lowest resistance possible for the site conditions which will permit the dissipation of a lightning discharge without causing damage.


D.
Attachments:



1.
Use copper lugs and stainless steel screws to attach conductor to fence post.  Drill and tap post.  Attach conductor to ground rod electrode with exothermic weld.



2.
Space fasteners not more than 3 feet apart on all conductors.



3.
Fasteners for existing masonry shall employ anchors having a diameter of not less than 1/4 inch.  Locate holes made to receive the shank of the fastener or fitting in the masonry rather than in the mortar joint when possible.  When set, the fit shall be tight against moisture and the effect of frost and capable of withstanding a pull test of 100 pounds.


E.
Surge Arresters:



1.
Install surge arresters on lightning surge arrester junction boxes where shown on drawings.



2.
Install one surge arrester on each conductor, including neutral, which enters junction box.

OMIT PARAGRAPH BELOW AND INCLUDE SECTION 310000 WHEN APPROPRIATE FOR THE EXTENT OF THE EARTHWORK REQUIRED.

F.
Excavation, Backfill and Restoration:  Excavate and backfill as required to install grounding system.  Restore lawns, pavement, walks, or other exterior surfaces displaced or marked by the Work of this Contract to their original conditions, as approved by the Director’s Representative.

3.02
FIELD QUALITY CONTROL


A.
System Acceptance Test:



1.
After system has been installed, take ground resistance reading for each ground electrode and record on approved test form.



2.
Submit test form with a plot plan drawing which indicates ground resistance for each electrode.

END OF SECTION

Updated 07/08/09

Printed 4/14/2015
337994 - 3
Project No. 


